## TOTAL PRICES
PRICE
| BUILDING NO | CIVIL WORKS | MECH. WORKS | ELECT. WORKS | TOTAL PRICE
1 | B01
2 | B01A
3 | B02
4 | B03
5 | B04
6 | B05
7 | B06
8 | B07
9 | B08
10 | B09
11 | B10
12 | B11
13 | B12
14 | B13
15 | B14
16 | B15
17 | B16
18 | B17
19 | B18
20 | B19
21 | B20
22 | B21
23 | B22
24 | B23
25 | B24-A
26 | B24-B
27 | B24-C
28 | B25
* | GENERAL REQUIREMENTS

## B-01 MECH
3. BILL OF QUANTITY-HYDRO (B-01)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
1.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 5.61 | 0 | 0
Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x2. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.48 | 0 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 6.16 | 0 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS |  |  |  | 0
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0 | 0
Calculation per piece.
TOTAL 1.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | [5 empty] | supply | apply
| Calculation per m of finished work | m1 | 31.33 | 0 | 0 |  | 28 | 114
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1
| Calculation per m of finished work |  | 44.43 | 0 | 0 |  | 18 | 96
3 | Supply and installation of steel galvanized water pipes Φ ¾ " (DN20mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for sanitaria. | m1
| Calculation per m of finished work. |  | 9.7 | 0 | 0 |  | 16 | 91
4 | Supply and installation of steel galvanized water pipes Φ ½ " (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for sanitaria. | m1
| Calculation per m of finished work. |  | 1.95 | 0 | 0 |  | 14 | 89
5 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc.
| Calculation per 1 pc. really built on the property. |  | 6 | 0 | 0 |  | 95 | 325
6 | Supply and installation of flat leaky ball valve Φ ½ "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc.
| Calculation per 1 pc. really built on the property. |  | 2 | 0 | 0 |  | 65 | 200
7 | Supply and installation of ball valves with lever and unions Φ 1 " | psc.
| Calculation per 1 pc. really built on the property. |  | 1 | 0 | 0 |  | 105 | 315
8 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 87.41 | 0 | 0 |  | 10 | 65
| Calculation per m1 finished work. |  | 87.41 | 0 | 0 |  | 3 | 12
TOTAL 1.3. ASSEMBLY WORK |  |  |  | 0
1.4 | SANITARY APPLIANCES AND SANITARY WARE
SANITARY APPLIANCES AND ACCESSORIES
Note:
The contractor should offer type and color of the sanitary equipment in agreement with an investor or an architect, and then approach contracting and total access and installation of the same order. Sanitary ware and fittings must be first-class (white), with chrome and feeders, like the type GEBERIT, GROHE, DOLOMITE, LAUFEN or equivalent. Ports-microclimate of supply and sanitary sewers run after approval by investors.
1 | Toilet bowl
Supply and installation of toilet bowls made of first class faience (sanitary ware), white color, and fully functional version with full plastic toilet cover and seat, toilet tank (low mounting) with angle valve and drain in the floor. Calculation per piece of fully installed toilet bowl.
|  | Psc | 1 | 0 | 0 |  | 780 | 1118
2 | Sink
Supply, transmission and assembly of first class faience sink, approx. 55 cm, together with chrome drainage tube and connecting material, one-hand mixer for hot and cold water, and angle valve Ø 1/2 "and all connecting material.
Calculation per piece of fully built sink.
|  | Psc | 1 | 0 | 0 |  | 220 | 1775
3 | Sanitary accessories
Supply and installation of sanitary ware (class I - INOX, or Kimberly-Clark or equivalent) with:
| a) toilet cleaning kit | Psc | 1 | 0 | 0 |  | 20 | 55
| b) toilet paper holder | Psc | 1 | 0 | 0 |  | 60 | 53
| c) wall mirror, dimensions 600 x 400 mm, thickness 4 mm, with polished edges | psc | 1 | 0 | 0 |  | 220 | 275
| d) paper towel holder | Psc
| e) bowl for liquid soap | Psc | 1 | 0 | 0 |  | 1000 | 995
TOTAL:
TOTAL 1.4 SANITARY APPLIANCES AND SANITARY WARE |  |  |  | 0
TOTAL 1. PLUMBING |  |  |  | 0
2. SEWAGE
1.1. EARTHWORKS
1 | Manual excavation of a trench width 80cm in materials of categories III and IV , along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.8 | 0 | 0 |  |  | 30
Calculation per m3 of finished work.
(2x0, 90x0, 6 x12.x12 +1.2) =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0 | 0 |  |  | 15
Calculation per m3 of finished work.
(2x0, 60x0, 2) =
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1 | 3.08 | 0 | 0 |  |  | 15
Calculation per m3 of finished work.
(2.81 to 0.24) x 1.2) =
TOTAL 2.1. EARTHWORKS |  |  |  | 0
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0 | 0 |  |  | 300
| Calculation per piece. | psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0 | 0 |  |  | 375
Calculation per piece.
| Providing drainage pipes to a height of 360 cm from the upper level of the flat roof. | psc | 1 | 0 | 0 |  |  | 855
size 25x25 cm
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
2.3 | ASSEMBLY WORK
Procurement of materials, transportation, installation, thermal insulation, functional and pressure test.
PVC sewer pipes for home sewers.
Supply and installation of PVC sewer pipes for the performance of internal sewage system, according to DIN 8061 and DIN 19531, with all necessary wiring and fittings and small installation material. Perform sealing sewer pipes with rubber rings. Bid to define the exact type of offered sewer, pipes with a certificate that guarantees the quality of pipes and fittings attached. Mandatory sample and approval before making the installation and approved by supervision, by the enrollment in the construction diary. Pipes of dubious quality, without adequate documentation, are forbidden to install. Mandatory photo documentation of built status before backfilling the trench in paragraph 1.1.).
This item includes all the work and all materials, pipe fittings, auxiliary material for joining and fixing - clips for fixed and sliding points.
Calculation per m of built sewers.
| DN 110 | m | 9.51 | 0 | 0 |  | 53 | 48
| DN 50 | m | 2.15 | 0 | 0 |  | 9 | 36
2 | PVC sewer revision / sweepers
Supply and installation of PVC sewer audit / sweepers for installation in the bottom of the control shaft AB.
Calculation per piece embedded audit / sweepers.
DN 110
|  | psc | 1 | 0 | 0 |  | 105 | 248
3 | TOP drainage tube
Procurement, supply and installation of the plastic top siphon with horizontal drains diameter Ø50 mm with a grid of stainless steel measuring 150 x 150 mm.
Calculation per piece integrated top siphon.
|  | psc | 1 | 0 | 0 |  | 115 | 301
4 | PVC ventilation cap
Supply and installation of vertical sewer vent caps, along with copper flashings including a link to waterproof (as type Braas or equivalent). Ventilation cap (set) Ø 50 mm.
Calculation per piece fitted caps.
|  | Psc | 1 | 0 | 0 |  | 1150 | 988
5 | Testing the building sewage
Testing of complete sewage facility with associated buildings pane and header tanks, etc. on the bandwidth and functionality. Testing performed prior to closing pipeline trenches and painting with photographic documentation of the required item 1.1. After successful completion of testing the functionality and impermeability, issue a certificate about the same. Development of rules / instructions on the operation and maintenance of the entire drainage system of the building is included in this item.
Calculation per m of tested network.
|  | m | 11.66 | 0 | 0 |  | 6 | 17
TOTAL 2.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 2. SEWAGE |  |  |  | 0
3. SPRINKLER NETWORK
3.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 3,1. EARTHWORKS |  |  |  | 0
3.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 2 | 0 | 0 |  |  | 375
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0 | 0 |  |  | 300
Calculation per piece.
TOTAL 3.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
3.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for emptying of sprinkler network, together with the associated fittings. Calculation per m of finished work | m1 | 13.33 | 0 | 0 |  | 33 | 104
2 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for drain line near signal valve according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 20.55 | 0 | 0 |  | 33 | 104
3 | Supply and installation of steel galvanized water pipes Φ 1 "(DN25mm), with the connections, for cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 53.53 | 0 | 0 |  | 28 | 95
4 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN32mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 48.78 | 0 | 0 |  | 36 | 101
5 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN40mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 12.94 | 0 | 0 |  | 38 | 109
6 | Supply and installation of galvanized steel plumbing Φ 2 "(DN50mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 7.78 | 0 | 0 |  | 50 | 122
7 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 30.82 | 0 | 0 |  | 85 | 213
8 | Supply and installation of water pipes ducktail Ø 4"together with associated fittings. Calculation per m of finished work. | m1 | 76.61 | 0 | 0 |  | 110 | 368
9 | Supply and installation of DUCTIL water pipes Ø 8“ together with associated | m1 | 8 | 0 | 0 |  | 200 | 709
10 | Supply control valve for the dry signal system on Ø 4“. | psc | 4 | 0 | 0 |  | 2100 | 3150
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 4 | 0 | 0 |  | 580 | 1370
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 4 | 0 | 0 |  | 3800 | 3550
13 | Supply of gate valve with oval body PN10 DN 100 | psc | 4 | 0 | 0 |  | 1100 | 1237
14 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network.
|  | psc | 1 | 0 | 0 |  | 1340 | 1848
15 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 1 | 0 | 0 |  | 150 | 329
16 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | psc | 1 | 0 | 0 |  | 1560 | 1628
17 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector).
|  | psc | 1 | 0 | 0 |  | 4780 | 5045
18 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc. | 4 | 0 | 0 |  | 380 | 916
19 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. Really built on the property. | psc. | 4 | 0 | 0 |  | 380 | 916
20 | Supply and installation of sprinkler Φ1" with capacity of 0,50 l/s Calculation per 1 pc. Really built on the property. | psc | 34 | 0 | 0 |  | 140 | 393
21 | Supply and installation of sprinkler Φ1" with capacity of 0,70 l/s Calculation per 1 pc. Really built on the property. | psc | 105 | 0 | 0 |  | 140 | 393
22 | Supply and installation of sprinkler Φ1" with capacity of 0,80 l/s Calculation per 1 pc. Really built on the property. | psc | 65 | 0 | 0 |  | 140 | 393
23 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 243.79 | 0 | 0 |  | 6 | 17
Calculation per m of finished work.
TOTAL 3.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 3. SPRINKLER NETWORK |  |  |  | 0
4. PRECIPITATOR
| 4.1. | EARTHWORKS
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 31.24 | 0 | 0 |  |  | 38
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 18.72 | 0 | 0 |  |  | 18
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 15.02 | 0 | 0 |  |  | 15
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 2.68 | 0 | 0 |  |  | 15
| TOTAL EARTHWORKS |  |  | 0
4.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 1.08 | 0 | 0 |  |  | 1350
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 3.86 | 0 | 0 |  |  | 1800
3 | Fabrication and installation of armor for the bottom plate and walls. |  | 31.24 | 0 | 0 |  |  | 1500
| MC 30 | Kg
| RA 400/500 | Kg
| TOTAL CONCRETE WORKS |  |  | 0
4.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 6 | 0 | 0 |  |  | 750
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | Psc | 2 | 0 | 0 |  |  | 1500
| Dim. 80x90 cm | Psc | 2 | 0 | 0 |  |  | 1500
| Dim. 80x95 | Psc | 2 | 0 | 0 |  |  | 1500
4.3 | TOTAL ASSEMBLY WORK |  |  | 0
4 | TOTAL PRECIPITATOR |  |  | 0
RECAPITULATION
| 1. PLUMBING |  |  | 0
| 2.SPRINKLER NETWORK |  |  | 0
| 3.SEWAGE |  |  | 0
| 4. PRECIPITATOR |  |  | 0
| Total: |  |  | 0
Machinery documentation(B-01)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling type KNND d50 18/09-FM, FTT, RPDTA, KDTA, L, VF***18/9-A, FTT, RPDTA, L, VF (flow 14760 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
- Section of plate recuperator with efficiency min 60% in summer period
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 14760 m3/hr, the external pressure drop 500 Pa
-Flexible connection
Drain part:
-Flexible connection
Suction-section of vertical air intake
Section-filtration fabric filter class F5
- section of plate recuperator efficiency min. 60% in summer period
-Section of ventilator with direct drive, vertical discharge in »Ex« execution, flow with two values 14760 m3/h, external pressure drop 500 Pa
-Flexible connector
|  | set | 1 | 0 | 0 |  | 38500 | 70940
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 105 kW at evaporating temperature and the outside temperature 50C to 460C
- 50 kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0 | 0 |  | 18000 | 21390
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
- automatic elements inside air conditioning chamber om antiexplosive design
|  | set | 1 | 0 | 0 |  | 24500 | 33820
4 | Axial ventilator as Klima Slovenia given in antiexplosive design
type AVS 355-4T-AO-B/Ex,
N=0,35 kW,n=1350 o/min.
| Exhaust grid with regulator in antiexplosive design size 250x500 | pcs | 2 | 0 | 0 |  | 1850 | 2110
|  | pcs | 4 | 0 | 0 |  | 1850 | 2110
5 | -Equipment of the system for humidifying air. In all of the EMA as Hr.
-Pump Station high pressure
Condair HP100 with VFD capacity of water
5 ÷ 200 kg / h, N = 0.5 kW
| -Droplet eliminator Condair HP | kom. | 1 | 0 | 0 |  | 17400 | 11970
size 600x300
| -System from the line with seven nozzles Condor HP capacity is 4.5 l / h | kom. | 3 | 0 | 0 |  | 16800 | 10425
-Condor 3 HP, valve block of 3 valves with seven degrees of ventilation
| -HST 010 duct humidity sensor | kom. | 3 | 0 | 0 |  | 1000 | 1475
-Condor HP Slave
| -Pipeline from f1/4'' | kom. | 3 | 0 | 0 |  | 150 | 197
| Complete with commissioning | kom. | 3 | 0 | 0 |  | 2100 | 1650
|  | kom. | 2 | 0 | 0 |  | 2100 | 1650
|  | met. | 40 | 0 | 0 |  | 6 | 32
6 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with sand
tipe APZR/ANŽ-4/3 size 1850x850
- exhaust exterior steel grate
Type AZR/ANŽ-4/3 size 1850x850
| -nozzle for square channel TŠ-5, | pcs | 1 | 0 | 0 |  | 420 | 404
size.315
size.400
| -ant-fire dampers for wall width L=750 | pcs | 1 | 0 | 0 |  | 420 | 404
PL-15 EL120S/A2/T12/Ex-Z
Size 900x500
| Size 600x350 | pcs. | 18 | 0 | 0 |  | 420 | 404
| Size 600x300 | Pcs | 9 | 0 | 0 |  | 420 | 404
Intake and exhaust grilles type AR-17 with two rows of blades and the flow regulator
| Size.625x325 | Pcs | 2 | 0 | 0 |  | 140 | 159
| Size 325x325 | Pcs | 2 | 0 | 0 |  | 140 | 159
| Size 525x225 | Pcs | 1 | 0 | 0 |  | 140 | 159
Size 525x175
size 425x175
| Size 325x175 | Pcs | 4 | 0 | 0 |  | 140 | 159
| Volume control damper RŽ-2/Ex-Z | Pcs | 2 | 0 | 0 |  | 310 | 320
| Size 500x350 | Pcs | 7 | 0 | 0 |  | 310 | 320
| Size.600x300 | Pcs | 9 | 0 | 0 |  | 310 | 320
| Size.400x400 | Pcs | 8 | 0 | 0 |  | 310 | 320
| Size.350x200 | Pcs | 2 | 0 | 0 |  | 310 | 320
|  | Pcs | 2 | 0 | 0 |  | 310 | 320
|  | Pcs | 1 | 0 | 0 |  | 310 | 320
|  | Pcs | 3 | 0 | 0 |  | 310 | 320
|  | Pcs | 1 | 0 | 0 |  | 310 | 320
7 | Galvanized sheet metal ducts of square and circular diameter of plate 0,8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 2200 | 0 | 0 |  | 9 | 41
8 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 220 | 0 | 0 |  | 80 | 175
9 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0 | 0 |  | 4000 | 8750
Total air cinditioning equipment: |  |  |  | 0
4.2 Equipment for compressed air
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0 | 0 |  | 19400 | 22897
2 | The docking reinforced flexible hose with couplings 1/2" L=1m
|  | pcs | 1 | 0 | 0 |  | 240 | 285
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 60 | 0 | 0 |  | 18 | 94
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
|  | pcs | 14 | 0 | 0 |  | 12 | 29
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 6 | 0 | 0 |  | 7 | 20
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 5 | 0 | 0 |  | 65 | 146
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 4 | 0 | 0 |  | 380 | 370
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 15 | 0 | 0 |  | 4 | 8
9 | Small materials for bonding, rosette of pipes, etc. | all inclusive | 1 | 0 | 0 |  | 1000 | 1250
10 | Pressure test the strength and tightness of compressed air installations | all iinclusive
|  |  | 1 | 0 | 0 |  | 100 | 650
Total equipment for compressed air: |  |  |  | 0
4.3. Thermal substation and thermal connection
No | An item of bill of quantities – thermal substation and thermal connection - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of exchanger thermal substation pipeline/pipeline capacity of Q=250 kW as type XB51H-1-60-2-25-AQ-1G2-1G2, Klase 1. od proizvođača «Danfoss».
With technical characteristics:
Water Primary Secondary
Flow rate m3/h 2.26; 6.62
Temperatures °C / °C 130.0/70.8 90.0 / 70.0
Pressure drop kPa 2 9
Dimensioning pressure bar 25 10
Pipes sizes (DN) 25 50
Total primary pressure drop kPa 36 kPa
Plate material EN 1.4404
Set contains:
- Generic control box, Metal, 3*400V, 1 pump, 401 W to 4 kW
- XB51-60H
- HEX_trans_insu_XB_51 60H_1_1_25_internal_description
- Danfoss, JIP-FF, Ball valve, PN40, DN32, Temp. max 180°C, DN32, Flange, Heating
- Danfoss, FVF - [64], kvs 20, PN25, DN32, Temp. max 200°C, DN32, Flange, Heating
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-160°C, L-50mm, Class 2.0, DN15, Welded, Both
- Pocket for thermometer sensor
- Water bag pipe steel DIN 16282/B U-Form angle, G 1/2"
- Danfoss, MDD80, 0-25 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- 3 way valve, 1/2 inch, Suku, Steel, Temp. Max 200C
- Generic muff, 1/2 inch, Inside thread, Both
- IVR, 660, PN25, DN15, Temp. max 200°C, 1/2 inch, Inside thread, Both
- Danfoss, AVQM, kvs 6.3, PN25, DN20, Temp. max 150°C, 1 inch, Outside thread, Heating
- Danfoss, AMV 23, with spring return, no spring up, 230V, Slow
- Generic muff, 1/2 inch, Inside thread, Both
- 3 way valve, 1/2 inch, Suku, Steel, Temp. Max 200C
- Water bag pipe steel DIN 16282/B U-Form angle, G 1/2"
- Danfoss, MDD80, 0-25 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- Pocket for thermometer sensor
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-160°C, L-50mm, Class 2.0, DN15, Welded, Both
- Danfoss, JIP-FF, Ball valve, PN40, DN25, Temp. max 180°C, DN25, Flange, Heating
- 1 " L=190
- Danfoss, JIP-WW, Ball valve, PN40, DN65, Temp. max 180°C, DN65, Welded, Heating
- Pocket for thermometer sensor
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-120°C, L-80mm, Class 2.0, DN15, Welded, Both
- Danfoss, MDD80, 0-10 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- 3 way valve for manometer, 1/2 inch, Tmax=150 C, standard
- Danfoss, FVF - [64], kvs 54, PN16, DN65, Temp. max 150°C, DN50, Flange, Heating
- IVR, 954, PN25, DN15, Temp. max 110°C, 1/2 inch, Inside thread, Both
- IVR, 954, PN25, DN15, Temp. max 110°C, 1/2 inch, Inside thread, Both
- Danfoss, Stainless steel pocket - 100 mm
- Danfoss, ESMU-100/Cu, PN25, Temp. max 140°C, Bo th
- Danfoss, ST-1, Both
- Syr, SYR 1915 DN20 5,5 BAR, max. 5.5 bar, 3/4 ", Inside thread, Both
- WILO, Stratos 40-1-12 (1,37), 1*230V
- 3 way valve for manometer, 1/2 inch, Tmax=150 C, standard
- Danfoss, MDD80, 0-10 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- Pocket for thermometer sensor
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-120°C, L-80mm, Class 2.0, DN15, Welded, Both
- Danfoss, VFY-WH, Butterfly valve, PN16, DN65, Temp. max 120°C, DN65, Inter flange, Heating
- Danfoss, ECL Comfort 110
- Danfoss, ESMT, Both
- Blank box component: Special Pocket for ST1 087N1201 _internal description
- HEX_bracket_XB51H_plates_6-60_internal_description
|  | set | 1 | 0 | 0 |  | 14000 | 20560
2 | Delivery and installation of closed expansion vessel with membrane with usable volume of 80 liters
|  | pcs | 1 | 0 | 0 |  | 400 | 1100
3 | Delivery and installation of collectors DN100:L=500mm with 1 pipe conncetros DN32; and 1 pipe conncetros DN 50, 1 pipe conncetros DN 65; NP10 in set with accessories for supporting
|  | set | 2 | 0 | 0 |  | 1100 | 1225
4 | Delivery and installation of collectors DN65:L=500mm with 2 pipe conncetros DN32, 1 pipe conncetros DN50; in set with accessories for supporting and thermal insulation.
0
|  | set | 2 | 0 | 0 |  | 1100 | 1263
5 | Delivery and installation of collectors DN50:L=500mm with 3 pipe conncetros DN15; and 1 pipe conncetros DN 32 NP10 in set with accessories for supporting and thermal insulation
|  | set | 2 | 0 | 0 |  | 1100 | 1263
6 | Delivery and installation of valve for warm water including sealing elements and bolts
| - DN 50 (2“); PN 16; | pcs | 4 | 0 | 0 |  | 99 | 335
| - DN 32 (5/4”); PN 16; | pcs | 8 | 0 | 0 |  | 85 | 246
| - DN 15 (5/4”); PN 16; | pcs | 6 | 0 | 0 |  | 65 | 190
|  | pcs | 6 | 0 | 0 |  | 12 | 26
7 | Delivery and installation of manometer, p = 0-10bar
8 | Delivery and installation of manometer 1/2", t=20÷150oC,
|  | pcs | 6 | 0 | 0 |  | 110 | 130
9 | Deliver, transport and installation of seamless steel pipes for the heating system. Inclusive:
| - Ф 21,3×2mm (DN 1/2") | m | 24 | 0 | 0 |  | 24 | 97
| - Ф 42,4×2,6mm (DN 5/4") | m | 84 | 0 | 0 |  | 28 | 113
| - Ф 57×2,9mm (DN 2") | m | 36 | 0 | 0 |  | 32 | 142
| - Ф 76,1×2,9mm (DN 2-1/2") | m | 12 | 0 | 0 |  | 90 | 170
10 | Supply and installation of thermal insulation of glass wool layer of aluminum sheet for steel pipe driven into the house, and warm-water channel to the terminal shaft
- for pipes fi 2-1/2"..........…. 12 m - for pipes fi 2".......…..… 36 m - for pipes fi 5/4"................. 84 m - for pipes fi 1/2".......….... . 24m
|  | set | 1 | 0 | 0 |  | 3600 | 3038
11 | Delivery and installation of steel arches, joints, supports and all other elements needed for making pipe installation (taken cca30% of the sum of the previous items 9 and 10)
All inclusive
|  |  | 1 | 0 | 0 |  | 1140 | 1110
12 | Cleaning, corrosion protection and painting of piping and supports anti-corrosion coatings resistant to elevated temperatures up to 200°C
|  | m2 | 30 | 0 | 0 |  | 8 | 22
13 | Testing the installation on the strength and tightness in all the technical requirements for pipelines and drafting minutes of testing.
All inclusive
|  |  | 1 | 0 | 0 |  | 1000 | 2750
14 | Marking the pipeline in terms of technological flows, development of functional schemes, instructions for use and maintenance of equipment subject | All inclusive | 1 | 0 | 0 |  | 250 | 500
15 | Preparatory finishing. This includes transportation and disposal of tools, equipment, crane vehicles and supplies for the safe and efficient performance of the installation work, security personnel and site against unsolicited intervention fails, fire, working at height, and so on.
All inclusive
|  |  | 1 | 0 | 0 |  | 500 | 1000
Total thermal substation and thermal pipline |  |  |  | 0
Total of all(B-01) MECH |  |  |  | 1142068.31 |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_01"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_01. (See related scheme 1.4.!) Following equipment have to be installed in main distribution cabinet:
| Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building! | [5 empty] | Supply | Installation
| All together | piece | 1 | 0 | 0 |  | 19800 | 17400 | 37200
TOTAL OF HIGH CURRENT: |  |  |  | 0
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
[7 empty] | Supply | Installation
| XP00- 4x150 mm2 (GRO -DO-TS) | m | 100 | 0 | 0 |  | 218.8 | 199.2 | 418
| XP00-A 4x50 mm2 (GRO -DO-TS) | m | 5 | 0 | 0 |  | 76.4 | 125.6 | 202
| XP00-A 4x35 mm2 | m | 35 | 0 | 0 |  | 59.1 | 116.9 | 176
| NHXH E60 4x25mm2 | m | 155 | 0 | 0 |  | 44 | 108 | 152
| PPOO 4x16mm2 | m | 15 | 0 | 0 |  | 30.8 | 101.2 | 132
| PPOO-Y 5x10 mm2 | m | 35 | 0 | 0 |  | 27.3 | 97.7 | 125
| PPOO-Y 5x2,5 mm2 | m | 120 | 0 | 0 |  | 9.8 | 89.2 | 99
| PPOO-Y 5x1,5 mm2 | m | 250 | 0 | 0 |  | 8.4 | 88.6 | 97
| PPOO-Y 3x2,5 mm2 | m | 140 | 0 | 0 |  | 4.3 | 85.7 | 90
| PPOO-Y 1x25 mm2 | m | 45 | 0 | 0 |  | 9.1 | 88.9 | 98
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
[7 empty] | Supply | Installation
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 80 | 0 | 0 |  | 75 | 132 | 207
3 | Sealing cables crossing between fire fireproof sector mass | kg | 20 | 0 | 0 |  |  | 15 | 15
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0 | 0 |  | 5000 | 2500 | 7500
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0 | 0 |  | 10000 | 5000 | 15000
TOTAL II : |  |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets) | [5 empty] | Supply | Installation
| PNK 100 | m | 60 | 0 | 0 |  | 29 | 75 | 104
| PNK 200 | m | 30 | 0 | 0 |  | 42 | 81 | 123
| Slat cable carriers 200 mm | m | 60 | 0 | 0 |  | 35 | 78 | 113
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 10 | 0 | 0 |  | 15 | 45 | 60
3 | Other small material | flat | 1 | 0 | 0 |  | 5000 | 2500 | 7500
TOTAL III: |  |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 49 | 0 | 0 |  | 680 | 790 | 1470
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 13 | 0 | 0 |  | 1500 | 1500 | 3000
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 4 | 0 | 0 |  | 890 | 895 | 1785
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 9 | 0 | 0 |  | 1300 | 1400 | 2700
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 1 | 0 | 0 |  | 580 | 740 | 1320
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 4 | 0 | 0 |  | 750 | 825 | 1575
7. | Other unspecified material needed for the installation | kpl | 1 | 0 | 0 |  | 5000 | 2500 | 7500
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0 | 0 |  | 10000 | 5000 | 15000
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 10 | 0 | 0 |  |  | 300 | 300
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 3 | 0 | 0 |  | 1500 | 1500 | 3000
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 20 | 0 | 0 |  | 4 | 64 | 68
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 25 | 0 | 0 |  |  | 75 | 75
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0 | 0 |  | 250 | 500 | 750
| .serial water-proof n/ž | piece | 1 | 0 | 0 |  | 300 | 525 | 825
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 2 | 0 | 0 |  | 200 | 475 | 675
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0 | 0 |  | 400 | 575 | 975
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0 | 0 |  | 450 | 600 | 1050
11 | Other small material | flat | 1 | 0 | 0 |  | 1000 | 6500 | 7500
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0 |  |  | 15000 | 15000
TOTAL V.1 : |  |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 11 | 0 | 0 |  | 8 | 72 | 80
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 6 | 0 | 0 |  | 150 | 450 | 600
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0 | 0 |  | 180 | 465 | 645
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 50 | 0 | 0 |  | 100 | 425 | 525
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0 | 0 |  | 100 | 425 | 525
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 3 | 0 | 0 |  | 140 | 445 | 585
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0 | 0 |  |  | 21750 | 21750
8. | Other small material | flat | 1 | 0 | 0 |  | 1000 | 11000 | 12000
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0 |  |  | 15000 | 15000
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0 | 0 |  | 1000 | 5000 | 6000
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 4 | 0 | 0 |  | 2000 | 11500 | 13500
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0 | 0 |  | 3500 | 1750 | 5250
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0 | 0 |  | 5.9 | 70.1 | 76
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 8 | 0 | 0 |  | 2750 | 4375 | 7125
6 | Creating bypass Gauge | piece | 1 | 0 | 0 |  |  | 7500 | 7500
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0 | 0 |  | 1000 | 6500 | 7500
8 | Testing of installed installations | pšl | 1 | 0 | 0 |  |  | 15000 | 15000
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 2 | 0 | 0 |  |  | 75
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 70 | 0 | 0 |  |  | 18
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0 | 0 |  |  | 964
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 2 | 0 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 30 | 0 | 0 |  | 12.7 | 74.3 | 87
| -PP00-Y 3x2,5 mm2 | m. | 6 | 0 | 0 |  | 4.3 | 63.7 | 68
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 30 | 0 | 0 |  | 50 | 250 | 300
| - PVC warning tape | met | 30 | 0 | 0 |  | 10 | 5 | 15
9 | Other small material for mounting and connecting | flat | 1 | 0 | 0 |  | 5000 | 2500 | 7500
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0 |  | 10000 | 5000 | 15000
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0 | 0 |  |  | 75 | 75
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0 | 0 |  | 13500 | 12750 | 26250
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0 | 0 |  | 9800 | 10900 | 20700
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0 | 0 |  | 7600 | 9050 | 16650
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 7 | 0 | 0 |  | 20000 | 10000 | 30000
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 7 | 0 | 0 |  | 7890 | 3945 | 11835
3. | Protective canopy drip-channel for detector. | piece | 7 | 0 | 0 |  | 6300 | 3150 | 9450
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0 | 0 |  | 4500 | 2250 | 6750
5. | Cable glands for Exd enclosure M25x15mm. | piece | 7 | 0 | 0 |  | 45 | 105 | 150
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 7 | 0 | 0 |  | 200 | 400 | 600
7. | Marking elements with persistent marks | piece | 7 | 0 | 0 |  | 500 | 250 | 750
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | 0 |  | 10000 | 5000 | 15000
TOTAL FLAME DETECTORS : |  |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 5 | 0 | 0 |  | 530 | 790 | 1320
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0 | 0 |  | 530 | 790 | 1320
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 2 | 0 | 0 |  | 650 | 850 | 1500
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0 | 0 |  | 650 | 850 | 1500
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0 | 0 |  | 650 | 850 | 1500
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0 | 0 |  | 1200 | 1350 | 2550
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0 | 0 |  | 1200 | 1350 | 2550
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0 | 0 |  | 1200 | 1350 | 2550
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0 | 0 |  | 800 | 1000 | 1800
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 18 | 0 | 0 |  | 800 | 1000 | 1800
11. | Supply and delivery of mark elements for the fire alarm system | piece | 17 | 0 | 0 |  | 500 | 250 | 750
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0 | 0 |  | 15000 | 7500 | 22500
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0 | 0 |  | 8000 | 4000 | 12000
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0 | 0 |  | 15000 | 7500 | 22500
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0 | 0 |  | 5000 | 2500 | 7500
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0 | 0 |  | 650 | 850 | 1500
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0 | 0 |  | 2500 | 1250 | 3750
18. | Marking elements with persistent marks | piece | 7 | 0 | 0 |  | 500 | 250 | 750
19. | Other unspecified fine material. | kpl. | 1 | 0 | 0 |  | 5000 | 2500 | 7500
20. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0 | 0 |  | 10000 | 5000 | 15000
TOTAL MANUAL TRANSMITTER |  |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | 0 |  | 530 | 715 | 1245
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0 | 0 |  | 2500 | 1250 | 3750
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0 | 0 |  | 50 | 250 | 300
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0 | 0 |  | 150 | 450 | 600
6. | Marking elements with persistant marks | piece | 2 | 0 | 0 |  | 500 | 250 | 750
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0 | 0 |  | 10000 | 5000 | 15000
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0 | 0 |  | 730 | 815 | 1545
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0 | 0 |  | 730 | 815 | 1545
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | 0 |  | 1200 | 1050 | 2250
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0 | 0 |  | 560 | 730 | 1290
5. | Marking elements with persistant marks | piece | 1 | 0 | 0 |  | 500 | 250 | 750
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0 | 0 |  | 5000 | 2500 | 7500
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 |  | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0 | 0 |  | 3500 | 2500 | 6000
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0 | 0 |  | 18000 | 12000 | 30000
| Cabinet includes: | piece | 1 | 0 | 0 |  | 28500 | 17250 | 45750
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0 | 0 |  | 730 | 815 | 1545
4. | Marking elements with persistent marks | piece | 2 | 0 | 0 |  | 500 | 250 | 750
5. | Other unspecified fine material. | kpl. | 1 | 0 | 0 |  | 5000 | 2500 | 7500
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | 0 |  | 10000 | 5000 | 15000
7. | ATTESTS FOR EX EQUIPMENT
Creating attests authorized by the domestic industry. |  |  |  | 0
TOTAL OF FIRE ALARM |  |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0 | 0 |  | 3500 | 4000 | 7500
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 4 | 0 | 0 |  | 5000 | 2500 | 7500
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0 | 0 |  | 5000 | 2500 | 7500
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0 | 0 |  | 100 | 200 | 300
5. | Other unspecified fine material. | kpl. | 1 | 0 | 0 |  | 5000 | 2500 | 7500
6. | Installation and connection of equipment | kpl. | 1 | 0 | 0 |  | 8000 | 4000 | 12000
| Total of Installation and connection of equipment |  |  | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0 | 0 |  | 85 | 104 | 189
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0 | 0 |  | 4 | 64 | 68
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 25 | 0 | 0 |  | 85 | 104 | 189
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0 | 0 |  | 65 | 94 | 159
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0 | 0 |  | 4 | 64 | 68
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0 | 0 |  | 4.3 | 63.7 | 68
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0 | 0 |  | 10 | 67 | 77
0
9. | Other unspecified fine material. | m. | 15 | 0 | 0 |  |  | 75 | 75
| TOTAL OF CABLE INSTALLATION |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl.
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
| . Handover and assembling the record on safety and functional testing. |  | 1 | 0 | 0 |  | 15000 | 7500 | 22500
| TOTAL COMMISSIONING : |  |  | 0
TOTAL IX
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 110 | 0 | 0 |  | 650 | 775 | 1425
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 6 | 0 | 0 |  | 2000 | 1450 | 3450
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 6 | 0 | 0 |  | 2000 | 1450 | 3450
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 6 | 0 | 0 |  | 650 | 775 | 1425
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 6 | 0 | 0 |  | 650 | 775 | 1425
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 6 | 0 | 0 |  | 100 | 50 | 150
Drip:
| KON 21; Rf 200212 | pieces | 12 | 0 | 0 |  | 650 | 775 | 1425
Impact point-Spitz:
| LOV Rf 300400 | pieces | 6 | 0 | 0 |  | 650 | 775 | 1425
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 12 | 0 | 0 |  | 1100 | 1000 | 2100
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 20 | 0 | 0 |  | 1100 | 1000 | 2100
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 4 | 0 | 0 |  | 1100 | 1000 | 2100
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 115 | 0 | 0 |  | 100 | 200 | 300
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 130 | 0 | 0 |  | 15 | 8 | 23
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 14 | 0 | 0 |  | 25 | 13 | 38
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 65 | 0 | 0 |  | 25 | 13 | 38
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0 | 0 |  | 10000 | 5000 | 15000
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0 | 0 |  | 10000 | 5000 | 15000
ELECTRICAL INSTALLATIONS - Recapitulation
1 | TOTAL OF HIGH CURRENT: |  |  | 0
2 | TOTAL OF POWER CABLES |  |  | 0
3 | AN INSTALLATION CABLE CARRIERS AND TUBES |  |  | 0
4 | TOTAL IV : |  |  | 0
5 | TOTAL V.1 : |  |  | 0
6 | TOTAL VI: |  |  | 0
7 | TOTAL VI: |  |  | 0
8 | TOTAL VII: |  |  | 0
9 | TOTAL VIII KM: |  |  | 0
10 | TOTAL IX: |  |  | 0
11 | TOTAL OF FIRE ALARM |  |  | 0
12 | TOTAL OF CABLE INSTALLATION |  |  | 0
13 | TOTAL COMMISSIONING : |  |  | 0
14 | LIGHTNING ROD INSTALLATION |  |  | 0
15 | TEST AND MEASURMENT |  |  | 0
14 | PROJECT OF CREATED STATE |  |  | 0
| TOTAL OF ELE |  |  |  |  | 0
TOTAL OF ELE+MECH | [5 empty] | 0

## B-01a MECH
3. BILL OF QUANTITY-HYDRO (B-01a)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
1.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0 | 0
Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x2. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS |  |  |  | 0
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 |  | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 |  | 0
Calculation per piece.
TOTAL 1.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN50mm), with the connections, cold water according to the plans of the project, together with associated fittings.
| Calculation per m of finished work | m1 | 11.09 | 0 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1
| Calculation per m of finished work |  | 12.64 | 0 | 0
3 | Supply and installation of flat leaky ball valve Φ 2 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc.
| Calculation per 1 pc. really built on the property. |  | 1 | 0 | 0
4 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc.
| Calculation per 1 pc. really built on the property. |  | 2 | 0 | 0
5 | Supply and installation of ball valves with lever and unions Φ 1 " | psc.
| Calculation per 1 pc. really built on the property. |  | 2 | 0 | 0
6 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1
| Calculation per m1 finished work. |  | 23.73 | 0 | 0
TOTAL 1.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 1. PLUMBING |  |  |  | 0
2. SEWAGE
1.1. EARTHWORKS
1 | Manual excavation of a trench width 80cm in materials of categories III and IV , along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.8 | 0 | 0
Calculation per m3 of finished work.
(2x0, 90x0, 6 x12.x12 +1.2) =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0 | 0
Calculation per m3 of finished work.
(2x0, 60x0, 2) =
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1 | 3.08 | 0 | 0
Calculation per m3 of finished work.
| (2.81 to 0.24) x 1.2) = |  |  | 0
TOTAL 2.1. EARTHWORKS |  |  |  | 0
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 |  | 0
| Calculation per piece. | psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 |  | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
2.3 | ASSEMBLY WORK
Procurement of materials, transportation, installation, thermal insulation, functional and pressure test.
1 | PVC sewer pipes for home sewers.
Supply and installation of PVC sewer pipes for the performance of internal sewage system, according to DIN 8061 and DIN 19531, with all necessary wiring and fittings and small installation material. Perform sealing sewer pipes with rubber rings. Bid to define the exact type of offered sewer, pipes with a certificate that guarantees the quality of pipes and fittings attached. Mandatory sample and approval before making the installation and approved by supervision, by the enrollment in the construction diary. Pipes of dubious quality, without adequate documentation, are forbidden to install. Mandatory photo documentation of built status before backfilling the trench in paragraph 1.1.).
This item includes all the work and all materials, pipe fittings, auxiliary material for joining and fixing - clips for fixed and sliding points.
Calculation per m of built sewers.
| DN 200 | m | 5.1 | 0 | 0
| DN 200 | m | 5.1 | 0 | 0
2 | Testing the building sewage
Testing of complete sewage facility with associated buildings pane and header tanks, etc. on the bandwidth and functionality. Testing performed prior to closing pipeline trenches and painting with photographic documentation of the required item 1.1. After successful completion of testing the functionality and impermeability, issue a certificate about the same. Development of rules / instructions on the operation and maintenance of the entire drainage system of the building is included in this item.
Calculation per m of tested network.
|  | m | 5.1 | 0 | 0
TOTAL 2.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 2. SEWAGE |  |  |  | 0
3. SPRINKLER NETWORK
3.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 3.1. EARTHWORKS |  |  |  | 0
3.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0 | 0
Calculation per piece.
TOTAL 3.2. MASONRY AND BRICKLAYERING WORK
3.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for discharge line according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 3.07 | 0 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for line which is for emptying of sprinkler network according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 4.05 | 0 | 0
3 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 27.03 | 0 | 0
4 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 13.56 | 0 | 0
5 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 1.23 | 0 | 0
6 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 8.61 | 0 | 0
7 | Supply and installation of water pipes ducktail Ø 4"together with associated fittings. Calculation per m of finished work. | m1 | 7 | 0 | 0
8 | Supply and installation of water pipes ducktail Ø 8"together with associated fittings. Calculation per m of finished work. | m1 | 16 | 0 | 0
9 | Supply control valve for the dry signal system on 3. " | psc | 1 | 0 | 0
10 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 1 | 0 | 0
11 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 1 | 0 | 0
12 | Supply of gate valve with oval body PN10 DN 80 | psc | 3 | 0 | 0
13 | Supply of gate valve with oval body PN10 DN 200 | psc | 1 | 0 | 0
14 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network.
|  | psc | 1 | 0 | 0
15 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 2.75 | 0 | 0
16 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | psc | 1 | 0 | 0
17 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector).
|  | psc | 1 | 0 | 0
18 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc. | 1 | 0 | 0
21 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1
| Calculation per m of finished work. |  | 113.57 | 0 | 0
TOTAL 3.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 3. SPRINKLER NETWORK |  |  |  | 0
4. PRECIPITATOR
4.1. | EARTHWORKS
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 31.24 | 0 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 18.72 | 0 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 15.02 | 0 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 2.68 | 0 | 0
TOTAL EARTHWORKS |  |  |  | 0
4.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 1.08 | 0 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 3.86 | 0 | 0
3 | Fabrication and installation of armor for the bottom plate and walls. |  | 31.24 | 0 | 0
| MC 30 | Kg
| RA 400/500 | Kg
TOTAL CONCRETE WORKS |  |  |  | 0
4.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 6 | 0 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | Psc | 2 | 0 | 0
| Dim. 80x90 cm | Psc | 2 | 0 | 0
| Dim. 80x95 | Psc | 2 | 0 | 0
4.3 | TOTAL ASSEMBLY WORK |  |  | 0
4 | TOTAL PRECIPITATOR |  |  | 0
RECAPITULATION
1. PLUMBING |  |  |  | 0
2.SPRINKLER NETWORK |  |  |  | 0
3. SEWAGE |  |  |  | 0
4. PRECIPITATOR |  |  |  | 0
Total: |  |  |  | 0
Machinery documentation(B-01)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit KNND d50 6/6-FM, FTT, RPDTA, KD, BD, L, VF***6/6-A, FTT, RPDTA, L, VF (2670 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 140C in summer
Section of the steam moisturizer with steam generator 30 kg / h
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 2670 m3 / h, the external pressure drop 500 Pa
-Flexible connection
Drain part:
-Flexible connection
Suction-section of vertical air intake
Section-filtration fabric filter class F5
- section of plate recuperator efficiency min. 60% in summer period
-Section of ventilator with direct drive, vertical discharge in »Ex« execution, flow with two values 2665 m3/h, external pressure drop 500 Pa
-Flexible connector
|  | set | 1 | 0 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 40 kW at evaporating temperature 5° and the outside temperature 460C
- 15kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
-elements of automation within the air chambers in the explosion-proof design
|  | set | 1 | 0 | 0
4 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 650x550
- exhaust exterior steel grate
Type AZR/ANŽ-4/3 size 650x550
- Diffuser for air supply with a box, model OD-11V/S/I19/Ex
| size 250 | pcs | 1 | 0 | 0
-air flow regulator MRP-1/Ex in front of OD-11/V
| Size 200 | pcs | 1 | 0 | 0
-nozzle square channel TS5, size160
breathable valve PV-160/2
| - Mounted box for the removal of air from the space type LN-3 from two strainer with filter F5 and manual control flow made ​​of stainless steel | pcs | 3 | 0 | 0
height h = 3400, port f 250
| fire-damper wall width L = 700 | pcs | 3 | 0 | 0
| PL-15 EL120S/A2/T12/Ex-Z | pcs | 5 | 0 | 0
| size300x200 | pcs | 6 | 0 | 0
size.400x250
-Pressure in suction grid as regulator
AR-17, size400x200
|  | pcs | 2 | 0 | 0
|  | pcs | 3 | 0 | 0
|  | pcs | 1 | 0 | 0
|  | pcs | 2 | 0 | 0
5 | Galvanized sheet metal ducts 0.80 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 450 | 0 | 0
6 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 55 | 0 | 0
7 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0 | 0
Total air conditioning equipment: |  |  |  | 0
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m | pcs
|  |  | 1 | 0 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 30 | 0 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 6 | 0 | 0
5 | Delivery and installation of galvanized steel pipe T pieces- T piece 1/2"
|  | pcs | 4 | 0 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 3 | 0 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 2 | 0 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 8 | 0 | 0
9 | Small materials for bonding, rosette for pipes, etc. | all inclusive | 1 | 0 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0 | 0
Total equipment for compressed air: |  |  |  | 0
Total of all(B-01)MECH |  |  |  | 378150.5 |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_01a"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_01a. (See related scheme 1.4.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0 | 0 |  | 0
| TOTAL : |  |  | 0
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x50 mm2 (GRO -DO-TS) | m | 5 | 0 | 0 |  | 0
| XP00-A 4x35 mm2 | m | 35 | 0 | 0 |  | 0
| NHXH E60 4x25mm2 | m | 20 | 0 | 0 |  | 0
| PPOO 4x16mm2 | m | 15 | 0 | 0 |  | 0
| PPOO-Y 5x10 mm2 | m | 20 | 0 | 0 |  | 0
| PPOO-Y 4x4 mm2 | m | 15 | 0 | 0 |  | 0
| PPOO-Y 5x2,5 mm2 | m | 120 | 0 | 0 |  | 0
| PPOO-Y 5x1,5 mm2 | m | 200 | 0 | 0 |  | 0
| PPOO-Y 3x2,5 mm2 | m | 140 | 0 | 0 |  | 0
| PPOO-Y 1x25 mm2 | m | 45 | 0 | 0 |  | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 80 | 0 | 0 |  | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 20 | 0 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0 | 0 |  | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0 | 0 |  | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0 | 0 |  | 0
| PNK 200 | m | 20 | 0 | 0 |  | 0
| Slat cable carriers 200 mm | m | 20 | 0 | 0 |  | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 10 | 0 | 0 |  | 0
3 | Other small material | flat | 1 | 0 | 0 |  | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 7 | 0 | 0 |  | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 4 | 0 | 0 |  | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 5 | 0 | 0 |  | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 3 | 0 | 0 |  | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 1 | 0 | 0 |  | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 3 | 0 | 0 |  | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0 | 0 |  | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0 | 0 |  | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 16 | 0 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 5 | 0 | 0 |  | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 20 | 0 | 0 |  | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 30 | 0 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0 | 0 |  | 0
| .serial water-proof n/ž | piece | 1 | 0 | 0 |  | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0 | 0 |  | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0 | 0 |  | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0 | 0 |  | 0
11 | Other small material | flat | 1 | 0 | 0 |  | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0 |  | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 4 | 0 | 0 |  | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 4 | 0 | 0 |  | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0 | 0 |  | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 50 | 0 | 0 |  | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0 | 0 |  | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 3 | 0 | 0 |  | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0 | 0 |  | 0
8. | Other small material | flat | 1 | 0 | 0 |  | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0 |  | 0
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0 | 0 |  | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 2 | 0 | 0 |  | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0 | 0 |  | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0 | 0 |  | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 6 | 0 | 0 |  | 0
6 | Creating bypass Gauge | piece | 1 | 0 | 0 |  | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0 | 0 |  | 0
8 | Testing of installed installations | pšl | 1 | 0 | 0 |  | 0
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 90 | 0 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 95 | 0 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm | m | 100 | 0 | 0
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 4 | 0 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 9 | 0 | 0 |  | 0
| -PP00-Y 3x2,5 mm2 | m. | 6 | 0 | 0 |  | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 30 | 0 | 0 |  | 0
| - PVC warning tape | met | 30 | 0 | 0 |  | 0
9 | Other small material for mounting and connecting | flat | 1 | 0 | 0 |  | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0 |  | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0 | 0 |  | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0 | 0 |  | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0 | 0 |  | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 2 | 0 | 0 |  | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 2 | 0 | 0 |  | 0
3. | Protective canopy drip-channel for detector. | piece | 2 | 0 | 0 |  | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0 | 0 |  | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 2 | 0 | 0 |  | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 2 | 0 | 0 |  | 0
7. | Marking elements with persistent marks | piece | 2 | 0 | 0 |  | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | 0 |  | 0
| TOTAL FLAME DETECTORS : |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 4 | 0 | 0 |  | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0 | 0 |  | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 2 | 0 | 0 |  | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0 | 0 |  | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0 | 0 |  | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0 | 0 |  | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0 | 0 |  | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0 | 0 |  | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0 | 0 |  | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 12 | 0 | 0 |  | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 12 | 0 | 0 |  | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0 | 0 |  | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0 | 0 |  | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0 | 0 |  | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0 | 0 |  | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0 | 0 |  | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0 | 0 |  | 0
18. | Marking elements with persistent marks | piece | 7 | 0 | 0 |  | 0
19. | Other unspecified fine material. | kpl. | 1 | 0 | 0 |  | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 3 | 0 | 0 |  | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | 0 |  | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0 | 0 |  | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0 | 0 |  | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0 | 0 |  | 0
6. | Marking elements with persistant marks | piece | 2 | 0 | 0 |  | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0 | 0 |  | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0 | 0 |  | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0 | 0 |  | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | 0 |  | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0 | 0 |  | 0
5. | Marking elements with persistant marks | piece | 1 | 0 | 0 |  | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0 | 0 |  | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0 | 0 |  | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0 | 0 |  | 0
| Cabinet includes: | piece | 1 | 0 | 0 |  | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0 | 0 |  | 0
4. | Marking elements with persistent marks | piece | 2 | 0 | 0 |  | 0
5. | Other unspecified fine material. | kpl. | 1 | 0 | 0 |  | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | 0 |  | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0 | 0 |  | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 4 | 0 | 0 |  | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0 | 0 |  | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0 | 0 |  | 0
5. | Other unspecified fine material. | kpl. | 1 | 0 | 0 |  | 0
6. | Installation and connection of equipment | kpl. | 1 | 0 | 0 |  | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0 | 0 |  | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0 | 0 |  | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 25 | 0 | 0 |  | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0 | 0 |  | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0 | 0 |  | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0 | 0 |  | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0 | 0 |  | 0
9. | Other unspecified fine material. | m. | 15 | 0 | 0 |  | 0
| total |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
| . Handover and assembling the record on safety and functional testing. |  |  |  | 0 |  | 0
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 35 | 0 | 0 |  | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 3 | 0 | 0 |  | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 3 | 0 | 0 |  | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 4 | 0 | 0 |  | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 3 | 0 | 0 |  | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 4 | 0 | 0 |  | 0
Drip:
| KON 21; Rf 200212 | pieces | 6 | 0 | 0 |  | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 4 | 0 | 0 |  | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 6 | 0 | 0 |  | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 10 | 0 | 0 |  | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 4 | 0 | 0 |  | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 7 | 0 | 0 |  | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 35 | 0 | 0 |  | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 250 | 0 | 0 |  | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 16 | 0 | 0 |  | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 20 | 0 | 0 |  | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0 | 0 |  | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0 | 0 |  | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE |  |  | 0
| CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
| TOTAL OF ELE |  |  | 0 |  | 0
TOTAL OF ELE+MECH | [5 empty] | 0
0

## B-02MECH
3. BILL OF QUANTITY-HYDRO (B-02)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
1.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning.
| Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x2. = | m3 | 2.81 | 0 | 0
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS |  |  |  | 0
1.2 | CONCRETE WORKS
1 | Making the connecting shafts of concrete, MB 20 in the corresponding panel. The size and shape of the detail. Perform treatment on walls and install creepers. | m3 | 1.1 | 0 | 0
1,2x1,2x0,35x1 + 0,8x0,75x1 =
| TOTAL 1,2 CONCRETE WORKS |  |  | 0
1.3. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0 | 0
Calculation per piece.
3 | Supply and installation of the cover size 80x80 with transport capacity of 25 tones. | psc | 1 | 0 | 0
Calculation per piece
TOTAL 1.3. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
1.4. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN50mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1
| Calculation per m of finished work |  | 11.65 | 0 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1
| Calculation per m of finished work |  | 6.17 | 0 | 0
3 | Supply and installation of flat leaky ball valve Φ 2 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc.
| Calculation per 1 pc. really built on the property. |  | 3 | 0 | 0
4 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc.
| Calculation per 1 pc. really built on the property. |  | 2 | 0 | 0
5 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1
| Calculation per m1 finished work. |  | 17.83 | 0 | 0
| TOTAL 1.4. ASSEMBLY WORK |  |  | 0
| TOTAL 1. PLUMBING |  |  | 0
2. SEWAGE
1.1. EARTHWORKS
1 | Manual excavation of a trench width 80cm in materials of categories III and IV , along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 0.59 | 0 | 0
Calculation per m3 of finished work.
(1,1x0,90x0,6) =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.31 | 0 | 0
Calculation per m3 of finished work.
(1x0, 60x0, 2) =
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1 | 0.55 | 0 | 0
Calculation per m3 of finished work.
0,59-0,13) x 1,2) =
| TOTAL 2.1. EARTHWORKS |  |  | 0
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0 | 0
| Calculation per piece. | psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0 | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
2.3 | ASSEMBLY WORK
Procurement of materials, transportation, installation, thermal insulation, functional and pressure test.
1 | PVC sewer pipes for home sewers.
Supply and installation of PVC sewer pipes for the performance of internal sewage system, according to DIN 8061 and DIN 19531, with all necessary wiring and fittings and small installation material. Perform sealing sewer pipes with rubber rings. Bid to define the exact type of offered sewer, pipes with a certificate that guarantees the quality of pipes and fittings attached. Mandatory sample and approval before making the installation and approved by supervision, by the enrollment in the construction diary. Pipes of dubious quality, without adequate documentation, are forbidden to install. Mandatory photo documentation of built status before backfilling the trench in paragraph 1.1.).
This item includes all the work and all materials, pipe fittings, auxiliary material for joining and fixing - clips for fixed and sliding points.
Calculation per m of built sewers.
| DN 200 | m | 1.1 | 0 | 0
2 | Testing the building sewage
Testing of complete sewage facility with associated buildings pane and header tanks, etc. on the bandwidth and functionality. Testing performed prior to closing pipeline trenches and painting with photographic documentation of the required item 1.1. After successful completion of testing the functionality and impermeability, issue a certificate about the same. Development of rules / instructions on the operation and maintenance of the entire drainage system of the building is included in this item.
Calculation per m of tested network.
|  | m | 1.1 | 0 | 0
TOTAL 2.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 2. SEWAGE |  |  |  | 0
3. SPRINKLER NETWORK
3.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 3.1. EARTHWORKS |  |  |  | 0
3.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0.05 | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0.005 | 0 | 0
Calculation per piece.
TOTAL 3.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
3.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for discharge line according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 4.97 | 0 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for line which is for emptying of sprinkler network according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 8.69 | 0 | 0
3 | Supply and installation of galvanized steel plumbing Φ 1 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 38.4 | 0 | 0
4 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN32mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 22.33 | 0 | 0
5 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN40mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 18.9 | 0 | 0
6 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 15.99 | 0 | 0
7 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 12.13 | 0 | 0
8 | Supply and installation of water pipes ducktail Ø 4"together with associated fittings. Calculation per m of finished work. | m1 | 21 | 0 | 0
9 | Supply and installation of water pipes ducktail Ø 8"together with associated fittings. Calculation per m of finished work. | m1 | 9 | 0 | 0
10 | Supply control valve for the dry signal system on Ø 3“. | psc | 2 | 0 | 0
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 2 | 0 | 0
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 2 | 0 | 0
13 | Supply of gate valve with oval body PN10 DN 80 | psc | 3 | 0 | 0
14 | Supply of gate valve with oval body PN10 DN 200 | psc | 1 | 0 | 0
15 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network.
|  | psc | 1 | 0 | 0
16 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 4.7 | 0 | 0
17 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | psc | 1 | 0 | 0
18 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector).
|  | psc | 1 | 0 | 0
19 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc. | 3 | 0 | 0
20 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1
| Calculation per m of finished work. |  | 167.89 | 0 | 0
TOTAL 3.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 3. SPRINKLER NETWORK |  |  |  | 0
4. PRECIPITATOR
4.1.
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 31.24 | 0 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 18.72 | 0 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 15.02 | 0 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 2.68 | 0 | 0
TOTAL EARTHWORKS |  |  |  | 0
4.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 1.08 | 0 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 3.86 | 0 | 0
3 | Fabrication and installation of armor for the bottom plate and walls. |  | 31.24 | 0 | 0
| MC 30 | Kg
| RA 400/500 | Kg
| TOTAL CONCRETE WORKS |  |  | 0
4.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 6 | 0 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | Psc | 2 | 0 | 0
| Dim. 80x90 cm | Psc | 2 | 0 | 0
| Dim. 80x95 | Psc | 2 | 0 | 0
4.3 | TOTAL ASSEMBLY WORK |  |  | 0
4 | TOTAL PRECIPITATOR |  |  | 0
RECAPITULATION
| 1. PLUMBING |  |  | 0
| 2.SPRINKLER NETWORK |  |  | 0
| 3.SEWAGE |  |  | 0
| 4. PRECIPITATOR |  |  | 0
| Total: |  |  | 0
Machinery documentation(B-01)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit type KNND d50 6/6-FM, FTT, RPDTA, KD, BD, L, VF***6/6-A, FTT, RPDTA, L, VF (2840 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
Section of the steam moisturizer with steam generator 30 kg / h
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 2840 m3 / h, the external pressure drop 500 Pa
|  | set | 1 | 0 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 20,3 kW at evaporating temperature 5° and the outside temperature 460C
- 15kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
-elements of automation within the air chambers in the explosion-proof design
|  | set | 1 | 0 | 0
4 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 650x550
- Mounted box for the removal of air from the space type LN-3 from two strainer with filter F5 and manual control flow made ​​of stainless steel
height h = 2300, port f 250
height h = 3000, port f 250
| - nozzle square channel TS5, size400 | pcs | 1 | 0 | 0
-fire-damper wall width L = 700
PL-15 EL120S/A2/T12/Ex-Z
Size 400x400
|  | pcs | 2 | 0 | 0
|  | pcs | 1 | 0 | 0
|  | pcs | 6 | 0 | 0
|  | pcs | 1 | 0 | 0
5 | Roof radial fan in explosion-proof as the Clima Celje type SVK2-450/400-4/6 type EX, N = 0.90 / 0.60 kW.
Some of the equipment cooling fan does
-elastic connection
self raising-blinds
-flange
-supporting structure for the pitched roof in thermal protection
Inverter-control speed
|  | set | 1 | 0 | 0
6 | Galvanized sheet metal ducts 0.80 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 450 | 0 | 0
7 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 65 | 0 | 0
7 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0 | 0
| Total air conditioning equipment: |  |  | 0
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m | pcs
|  |  | 1 | 0 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 18 | 0 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 6 | 0 | 0
5 | Delivery and installation of galvanized steel pipe T pieces- T piece 1/2"
|  | pcs | 4 | 0 | 0
6 | Supply and installation of valves for compressed air with connection for flexible hose.
- R 1/2"
|  | pcs | 2 | 0 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 1 | 0 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 6 | 0 | 0
9 | Small materials for bonding, rosette for pipes, etc. | all inclusive | 1 | 0 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0 | 0
| Total equipment for compressed air: |  |  | 0
Total of all(B-01)MECH |  |  |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_02"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_02. (See related scheme 1.7.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0 | 0
TOTAL :
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x50 mm2 (GRO -DO-TS) | m | 50 | 0 | 0
| XP00-A 4x35 mm2 | m | 10 | 0 | 0
| NHXH E60 4x25mm2 | m | 20 | 0 | 0
| PPOO 4x16mm2 | m | 15 | 0 | 0
| PPOO-Y 5x10 mm2 | m | 15 | 0 | 0
| PPOO-Y 5x2,5 mm2 | m | 10 | 0 | 0
| PPOO-Y 5x1,5 mm2 | m | 20 | 0 | 0
| PPOO-Y 3x2,5 mm2 | m | 10 | 0 | 0
| PPOO-Y 1x25 mm2 | m | 25 | 0 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 90 | 0 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 20 | 0 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0 | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 14 | 0 | 0
| PNK 200 | m | 20 | 0 | 0
| Slat cable carriers 200 mm | m | 20 | 0 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 10 | 0 | 0
3 | Other small material | flat | 1 | 0 | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 13 | 0 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 4 | 0 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 1 | 0 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 1 | 0 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 2 | 0 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 1 | 0 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0 | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 20 | 0 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 2 | 0 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 20 | 0 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 30 | 0 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0 | 0
| .serial water-proof n/ž | piece | 1 | 0 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0 | 0
11 | Other small material | flat | 1 | 0 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 4 | 0 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 4 | 0 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 20 | 0 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 2 | 0 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 4 | 0 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0 | 0
8. | Other small material | flat | 1 | 0 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 2 | 0 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 6 | 0 | 0
6 | Creating bypass Gauge | piece | 1 | 0 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0 | 0
8 | Testing of installed installations | pšl | 1 | 0 | 0
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 40 | 0 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 40 | 0 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 2 | 0 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm | m | 45 | 0 | 0
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 2 | 0 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 45 | 0 | 0
| -PP00-Y 3x2,5 mm2 | m. | 12 | 0 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 30 | 0 | 0
| - PVC warning tape | met | 30 | 0 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0 | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 4 | 0 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 4 | 0 | 0
3. | Protective canopy drip-channel for detector. | piece | 4 | 0 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 4 | 0 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 4 | 0 | 0
7. | Marking elements with persistent marks | piece | 4 | 0 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | 0
| TOTAL FLAME DETECTORS : |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 3 | 0 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 2 | 0 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 6 | 0 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 6 | 0 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0 | 0
18. | Marking elements with persistent marks | piece | 6 | 0 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 3 | 0 | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0 | 0
6. | Marking elements with persistant marks | piece | 2 | 0 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0 | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0 | 0
5. | Marking elements with persistant marks | piece | 1 | 0 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0 | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0 | 0
| Cabinet includes: | piece | 1 | 0 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0 | 0
4. | Marking elements with persistent marks | piece | 2 | 0 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 4 | 0 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 25 | 0 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 35 | 0 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 35 | 0 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0 | 0
9. | Other unspecified fine material. | m. | 15 | 0 | 0
| sub total |  |  | 0
| total fire alarm |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
| . Handover and assembling the record on safety and functional testing. |  |  | 0
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 50 | 0 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 3 | 0 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 3 | 0 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 4 | 0 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 3 | 0 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 4 | 0 | 0
Drip:
| KON 21; Rf 200212 | pieces | 6 | 0 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 3 | 0 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 5 | 0 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 7 | 0 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 4 | 0 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 3 | 0 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 50 | 0 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 150 | 0 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 16 | 0 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 37 | 0 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
TOTAL OF ELE
TOTAL OF ELE+MECH |  |  |  | 0

## B-03-04 MECH
3. BILL OF QUANTITY-HYDRO (B-03-04)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. SPRINKLER NETWORK
1.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3 | 5.61 | 0
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.48 | 0
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1 | 6.16 | 0
Calculation per m3 of finished work.
| TOTAL 1.1. EARTHWORKS |  |  | 0
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | kom
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
| TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  | 0
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, water supply for washing objects together with the associated fittings. Calculation per m of finished work | m1
|  |  | 44.68 | 0
1 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, for emptying of sprinkler network according to project plan, together with the associated fittings. Calculation per m of finished work | m1
|  |  | 7.76 | 0
3 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 53.1 | 0
4 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 19.1 | 0
5 | Supply and installation of steel galvanized water pipes Φ 2" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1
| Calculation per m of finished work. |  | 3.06 | 0
6 | Supply and installation of steel galvanized water pipes Φ 3" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1
| Calculation per m3 of finished work. |  | 27.47 | 0
7 | Supply and installation of water pipes ducktil Ø 4 " together with associated fittings. Calculation per m of finished work.. | m1 | 22 | 0
9 | Supply and installation of water pipes ducktil Ø 8 " together with associated fittings. Calculation per m of finished work. | m1 | 12 | 0
10 | Supply of control signal valve for system Ø 4“. | kom | 1 | 0
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | kom | 1 | 0
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | kom | 1 | 0
13 | Supply of gate valve with oval body PN10 DN 100 | kom | 3 | 0
14 | Supply and installation of non-return valve diameter Ø 4 " at the inlet line for sprinkler network.
|  | kom | 1 | 0
15 | Supply and installation of non-return valve diameter Ø 3 " at the inlet line for sprinkler network.
|  | kom | 1 | 0
16 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 6.55 | 0
17 | Supply and installation of non-return valve Ø 3” at the inlet lines for fire trucks.
|  | kom | 1 | 0
18 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector).
|  | kom | 1 | 0
19 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property. | kom. | 4 | 0
20 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. really built on the property. | kom. | 4 | 0
21 | Supply and installation of sprinkler Φ1"with capacity of 0,87 l/s Calculation per 1 pc. really built on the property. | kom | 69 | 0
23 | Testing by placing plumbing network under test pressure of 15 bars. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1
| Calculation per m of finished work |  | 215.67 | 0
TOTAL 2.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 2. SPRINKLER NETWORK |  |  |  | 0
3. SEWAGE
Sewage consists of drains with grids that are considered in Construction part of the project.
RECAPITULATION
1. PLUMBING
2 SPRINKLER NETWORK |  |  |  | 0
Total: |  |  |  | 0
Machinery documentation(B-03-04)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit like types: KNNL d50 9/9-FM, FTT, KDTA, L, VF (4750 m3/h) from Slovenia «Hidria» completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 100C /59% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 4750 m3/h, the external pressure drop 500 Pa
-Flexible connection
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 45 kW at evaporating temperature and the outside temperature 50C to 460C
- 30kW heating capacity at outside temperature 0C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
|  | set | 1 | 0
4 | Roof radial fan in the anti-explosive performance as the Clima Celje, Slovenia.
SVK2-400/315-4/6 types: EX, N = 0.66 / 0.45 kW.
Some of the equipment cooling fan are:
- Flexible connector
- Auto -lift shutters
- Flange
- Supporting structure for the pitched roof in thermal protection
- Frequency regulator for speed control
|  | set | 2 | 0
5 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
APZR/ANŽ-4/3 types: size 950x850
- Diffuser for air supply with a box, model
OD-11V/S/I19/Ex in the panel 600x600 mm
| size 200 | pcs | 1 | 0
- Mechanical air flow regulator MRP-1/Ex placed in front of the diffuser OD-11, Ф 160
- Diffuser for air supply model OD-11V/Ex size 315
| - Mounted diffuser made ​​of stainless steel SD1/F1,H=1250, Ф 200 | pcs | 11 | 0
SD2/F1,H=1250, Ф 200
| - Mechanical air flow regulator MRP-1/Ex placed in front of the diffuser SD1 and SD 2, Ф 200 | pcs | 11 | 0
- Fire damper wall width L = 400
| PL-15 EL120S/A2/T12/Ex-Z | pcs | 3 | 0
size 800x400
|  | pcs | 2 | 0
|  | pcs | 2 | 0
|  | pcs | 4 | 0
|  | pcs | 1 | 0
6 | Galvanized sheet metal ducts of square and circular diameter of plate 0.8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg | 550 | 0
7 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
- Ф250
|  | m1 | 25 | 0
8 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 95 | 0
9 | Fine regulation, commissioning, testing capacity and quantity.
|  | commissioning | 1 | 0
10 | Local air conditioning as of the LG Electronics
Internal unit:
AH 07 AH N40 (Qc/h=2,1/2,4 kW) kom.3
AH 09 AH N40 (Qc/h=2,5/2,9 kW) kom.1
External unit:
MU 5M 30 (Qc/h=8,8/10,1 kW) kom.1
Equipment for connection and commissioning.
| Set | set | 1 | 0
| Total equipment for air conditioning: |  |  | 0
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m
|  | kom | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 60 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
|  | pcs | 14 | 0
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 6 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 5 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | kom | 4 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | kom | 15 | 0
9 | Small materials for bonding, rozetne of pipes, etc. | all inclusive | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
| Total equipment for compressed air: |  |  | 0
No | An item of bill of quantities –heat substation- delivery, transportation, assembly- | Unit of measure | Quantity | Total price
11 | Heat substation
Fin heat exchanger of 40 kW
- Primary side water 130/900C, dp = 2000P
- Secondary side water 90/700C, dp = 1500pa
Armour of substation
Valve with unions NP16
- R-1'', kom.4
-Fill & drain R ½'' kom.2
Control circuit hot water
-regulating circuit,
- Electric line valve R 1'',
- Limit thermostat 900C,
- Initial temperature sensor,
- Spatial sensor
- Circulation pump Wilo
Star RS 25/8, N = 0.157 kW
- Expansion vessel shut V = 15 lit with sig. valve R1 / 2''
- Pressure gauge 0-6 bar,
- Pressure gauge 0-16 bar,
- Thermometer 0-1200C AM,
- Thermometer 0-1800C,
- Connecting a secondary piping F1'' length l = 6m
| set | set | 1 | 0
Note: the primary pipeline is not subject of bill of quantities (provided by the investor)
| Total heat substation: |  |  | 0
Total of all(B-01)MECH |  |  |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | MAIN DISTRIBUTION CABINET "GRO-B3"
1 | Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks GRO-RO-B3. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet :
Section of grid voltage
1.2. | DISTRIBUTION CABINET "RO.B_3"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_3. (See related scheme 103.2.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
TOTAL :
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x95 mm2 (GRO -DO-TS) | m | 100 | 0
| NHXH E60 4x70 mm2 | m | 30 | 0
| PPOO 4x35mm2 | m | 35 | 0
| PPOO-Y 5x16 mm2 | m | 15 | 0
| PPOO-Y 5x10 mm2 | m | 25 | 0
| PPOO-Y 5x6 mm2 | m | 1 | 0
| PPOO-Y 5x2,5 mm2 | m | 10 | 0
| PPOO-Y 5x1,5 mm2 | m | 1 | 0
| PPOO-Y 3x2,5 mm2 | m | 50 | 0
| PPOO-Y 1x70 mm2 | m | 36 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 180 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 10 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0
| PNK 200 | m | 20 | 0
| PNK 300 | m | 45 | 0
| Slat cable carriers 200 mm | m | 2 | 0
| Slat cable carriers 300 mm | m | 2 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 28 | 0
3 | Other small material | flat | 1 | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 18 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 10 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 7 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 5 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 6 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 5 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 42 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 12 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 40 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 100 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 5 | 0
| .serial water-proof n/ž | piece | 5 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0
| SKX 12/22 Serial switch SMS 03/8 - switch actuator SMO 17/5 - cable gland SPU 25, Type: SKX 12/22, TEP | piece | 1 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 10 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 4 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 15 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 5 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 50 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 3 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 7 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 10 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
TOTAL VII:
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 3 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 120 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 3 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 3 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 130 | 0
| -PP00-Y 3x2,5 mm2 | m. | 22 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 125 | 0
| - PVC warning tape | met | 130 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 4 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 4 | 0
3. | Protective canopy drip-channel for detector. | piece | 4 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 4 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 4 | 0
7. | Marking elements with persistent marks | piece | 4 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
| TOTAL FLAME DETECTORS : |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 5 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
| Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 10 | 0
3 | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 2 | 0
4 | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0
5 | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0
6 | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 5 | 0
7. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
8. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
9. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 16 | 0
10. | Supply and delivery of mark elements for the fire alarm system | piece | 16 | 0
11. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
12. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
13. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
14. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
15. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
16. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
17. | Marking elements with persistent marks | piece | 16 | 0
18. | Other unspecified fine material. | kpl. | 1 | 0
19. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 3 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 3 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 3 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 3 | 0
6. | Marking elements with persistant marks | piece | 3 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 7 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 2 | 0
5. | Marking elements with persistant marks | piece | 2 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 2 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
· 1 piece of the Power supply unit 24V, 5A,
· 1 piece of the rechargeable battery 2x12V, 7,2Ah,
· 1 piece of the automatic fuse 6A,
· relay vard with three relays 24V/2A
· 40 pieces of Two-stairs VS terminals 1.5mm2,
· spaces for safety barriers
· spaces for MDI module
· spaces for SOM module
· 1 piece of the. DIN šina,
· perforated tiles with lid
· other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 11 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 10 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 10 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 20 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 78 | 0
9. | Other unspecified fine material. | m. | 15 | 0
| sub total fire alarm |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
| TOTAL COMMISSIONING : |  |  | 0
TOTAL IX
| total fire alarm |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 220 | 0
Roof equipment:
Wall cabinet for measurement:
ZON 05, Rf 20522
| Wall brackets (for the height difference): |  | 8 | 0
ZON 03, Rf20322
|  | pieces | 12 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 30 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 8 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 8 | 0
Drip:
| KON 21; Rf 200212 | pieces | 8 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 9 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 8 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 30 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 7 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 7 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 230 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 650 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 80 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 300 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
| TOTAL OF ELE |  |  | 0
TOTAL OF ELE+MECH |  |  |  | 0

## B-05 MECH
3. BILL OF QUANTITY-HYDRO (B-05)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
1.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work. 2x0,90x0,6+1.2x12.x12. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work. 2x0,60x0,2
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work (2,81-0,24) x 1,2
| TOTAL 1.1. EARTHWORKS |  |  | 0
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 1.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1
| Calculation per m of finished work |  | 26.44 | 0
2 | Supply and installation of flat leaky ball valve Φ 1" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | pcs
| Calculation per 1 pc. really built on the property. |  | 2 | 0
3 | Supply and installation of ball valves with lever and unions Φ 1 " | pcs
| Calculation per 1 pc. really built on the property. |  | 1 | 0
4 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 26.44 | 0
Calculation per m1 finished work.
TOTAL 1.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 1. PLUMBING PIPELINE |  |  |  | 0
2. SPRINKLERS NETWORK
2.1. EARTHWORKS
The calculation is performed by plumbing works, because the installation of water and hydrant network laid in the same trench.
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3
Calculation per m3 of finished work
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3of finished work.
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1
Calculation per m3of finished work.
| TOTAL 2.1. EARTHWORKS |  |  | 0
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0.001 | 0
| Calculation per piece. | psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0.001 | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1" (DN32mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1
| Calculation per m of finished work |  | 2.98 | 0
2 | Supply and installation of steel galvanized water pipes Φ | m1
" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings.
| Calculation per m of finished work. |  | 18 | 0
3 | Supply and installation of steel galvanized water pipes Φ | m1
" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings.
| Calculation per m of finished work. |  | 16 | 0
4 | Supply and installation of steel galvanized water pipes Φ 2" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1
| Calculation per m of finished work. |  | 20 | 0
5 | Supply and installation of steel galvanized water pipes Φ 3" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1
| Calculation per m of finished work. |  | 4 | 0
6 | Supply and installation of ducktil water pipes Φ 4" together with associated fittings. | m1
Calculation per m1 of finished work.
|  |  | 20 | 0
7 | Supply of control signal valve for wet system Ø 4“. | pcs | 1 | 0
8 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | pcs | 1 | 0
9 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | pcs | 1 | 0
10 | Supply of gate valve with oval body PN10 DN 100 | psc | 2 | 0
| GATE VALVE WITH OVAL BODY |  | 2 | 0
11 | Supply and installation of non-return valve diameter 4 " at the inlet line for sprinkler network.
|  | psc | 1 | 0
12 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 5.82 | 0
13 | Supply and installation of non-return valve Ø 3” at the inlet lines for fire trucks.
|  | psc | 1 | 0
14 | Supply and installation of connectors for connection Ø 3 fire engines "(double type connector).
|  | psc | 1 | 0
15 | Supply and installation of flat leaky ball valve Φ 1" in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property. | psc | 1 | 0
16 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. Really built on the property. | psc | 1 | 0
17 | Supply and installation of sprinkler Φ1" with capacity of 0,93 l/s. Calculation per 1 pc. Really built on the property. | psc
|  |  | 44 | 0
18 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1
| Calculation per m of finished work |  | 111.1 | 0
TOTAL 2.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 2. SPRINKLER NETWORK |  |  |  | 0
3. SEWAGE
EARTHWORKS
1 | Excavation of earth category III mechanical way at a depth of 0-3.5 m with rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 15.62 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 9.36 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. (15,62 – 9,36)x1,20 | m3 | 7.51 | 0
4 | Supply, filling and compacting gravel for the bottom plate surface at a thickness of septic 20 cm | m3 | 1.34 | 0
TOTAL EARTHWORKS |  |  |  | 0
3.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 0.54 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 1.93 | 0
3 | Fabrication and installation of armor for the bottom plate and walls.
| MC 30 | Kg
| RA 400/500 | Kg
TOTAL CONCRETE WORKS |  |  |  | 0
3.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | psc | 3 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | psc | 1 | 0
| Dim. 80x90 cm | psc | 1 | 0
| Dim. 80x95 | psc | 1 | 0
| TOTAL ASSEMBLY WORK |  |  | 0
3 | TOTAL SEWAGE |  |  | 0
RECAPITULATION
| 1. PLUMBING |  |  | 0
| 2.SPRINKLER NETWORK |  |  | 0
| 3.SEWAGE |  |  | 0
| Total: |  |  | 0
Machinery documentation(B-05)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit like types: KNNL d50 6/6-FM, FTT, KD,BD, L, VF (2200 m3/h) from Slovenia «Hidria» completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /59% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 350C in summer
- Section of the steam humidifier with steam generator 20 kg/h
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 2200m3/h, the external pressure drop 500 Pa
-Flexible connection
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 10kW at evaporating temperature and the outside temperature 50C to 460C
- 12kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
-automatic elements inside of the air conditioning chamber in anti-explosive performance
|  | set | 1 | 0
4 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
APZR/ANŽ-4/3 types: size 650x550
- Diffuser for air supply with a box, model
OD-11V/S/I19/Ex in the panel 600x600 mm
| size 200 | pcs | 1 | 0
- Mechanical air flow regulator MRP-1/Ex placed in front of the diffuser OD-11, F 160
- Fire damper wall width L = 500
PL-15 EL120S/A2/T12/Ex-Z
| size 500x250 | pcs | 7 | 0
-External inox grid with protective inox network with auto-lifting Venetian blinds from aluminum sheet, size 500x300
|  | pcs | 7 | 0
|  | pcs | 1 | 0
|  | pcs | 4 | 0
5 | Galvanized sheet metal ducts of square and circular diameter of plate 0.8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg | 250 | 0
6 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
- Ф160
|  | m1 | 20 | 0
7 | Insulation of sheet metal channels outside the with hard mineral wool 100mm, coated in sheet inox metal
Calculated per m2
|  | m2 | 6 | 0
8 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 40 | 0
9 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
| Total equipment for air conditioning: |  |  | 0
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m
|  | kom | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 18 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 8 | 0
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 2 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 1 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | kom | 1 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | kom | 5 | 0
9 | Small materials for bonding, rozetne of pipes, etc. | all inclusive
|  |  | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
Total equipment for compressed air: |  |  |  | 0
Total of all(B-01)MECH
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | MAIN DISTRIBUTION CABINET "GRO-B3"
1 | Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks GRO-RO-B3. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet :
Section of grid voltage
1.2. | DISTRIBUTION CABINET "RO.B_3"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_3. (See related scheme 103.2.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
| TOTAL : |  |  | 0
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x95 mm2 (GRO -DO-TS) | m | 100 | 0
| PPOO 4x35mm2 | m | 25 | 0
| PPOO-Y 5x16 mm2 | m | 15 | 0
| PPOO-Y 5x10 mm2 | m | 12 | 0
| PPOO-Y 5x2,5 mm2 | m | 10 | 0
| PPOO-Y 3x2,5 mm2 | m | 20 | 0
| PPOO-Y 1x35 mm2 | m | 25 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 100 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 7 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0
| PNK 200 | m | 30 | 0
| PNK 300 | m | 20 | 0
| Slat cable carriers 200 mm | m | 30 | 0
| Slat cable carriers 300 mm | m | 20 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 15 | 0
3 | Other small material | flat | 1 | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The floodlight is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air.Hazardous zones: 1,2, 21, 22. Housing: aluminium powder painted casting Diffuser: borosilicate tube glass, IP 66 in accordance with EN 60529+A1, category 1, RLF/250 HST, 250 W Accessories: protected galvanized steel gird, assembly kit for wall, pipe and ceiling mounting Ex de IIC T4-T3 or Ex d IIC T4-T3 tD A21 IP66 T10ºC-150ºC, 231V, 60 Hz, | piece | 2 | 0
2. | The floodlight is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air.Hazardous zones: 1,2, 21, 22. Housing: aluminium powder painted casting Diffuser: borosilicate tube glass, IP 66 in accordance with EN 60529+A1, category 1, RLF/85 QL, 85 W Accessories: protected galvanized steel gird, assembly kit for wall, pipe and ceiling mounting Ex de IIC T4-T3 or Ex d IIC T4-T3 tD A21 IP66 T10ºC-150ºC, 231V, 60 Hz, | piece | 2 | 0
3. | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 3 | 0
5. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 1 | 0
6. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 1 | 0
7. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 1 | 0
8. | Other unspecified material needed for the installation | kpl | 1 | 0
9. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 14 meters. | piece | 7 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 3 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 20 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 30 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0
| .serial water-proof n/ž | piece | 1 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 2 | 0
| SKX 12/22 Serial switch SMS 03/8 - switch actuator SMO 17/5 - cable gland SPU 25, Type: SKX 12/22, TEP | piece | 1 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 11 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 5 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 20 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 1 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 1 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 2 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 10 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 10 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | m | 3 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 1 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 170 | 0
| -PP00-Y 3x2,5 mm2 | m. | 37 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 150 | 0
| - PVC warning tape | met | 150 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version. | piece | 2 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 2 | 0
3. | Protective canopy drip-channel for detector. | piece | 2 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
7. | Marking elements with persistent marks | piece | 2 | 0
Other unspecified fine material.
0
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
| TOTAL FLAME DETECTORS : |  |  | 0
0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 3 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
| Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 1 | 0
3 | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0
4 | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-, II 2 G Ex ib IIC T4,IP-54SECURITON | piece | 1 | 0
5 | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 1 | 0
6 | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 5 | 0
7. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
8. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
9. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 9 | 0
10. | Supply and delivery of mark elements for the fire alarm system | piece | 9 | 0
11. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
12. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
13. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
14. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
15. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
16. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
17. | Marking elements with persistent marks | piece | 16 | 0
18. | Other unspecified fine material. | kpl. | 1 | 0
19. | Installation and connection of the detector, all the EX version. | kpl. | 1 | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0
6. | Marking elements with persistant marks | piece | 1 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 2 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 2 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 2 | 0
0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
· 1 piece of the Power supply unit 24V, 5A,
· 1 piece of the rechargeable battery 2x12V, 7,2Ah,
· 1 piece of the automatic fuse 6A,
· relay vard with three relays 24V/2A
· 40 pieces of Two-stairs VS terminals 1.5mm2,
· spaces for safety barriers
· spaces for MDI module
· spaces for SOM module
· 1 piece of the. DIN šina,
· perforated tiles with lid
· other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 5 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 3 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 5 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 5 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0
9. | Other unspecified fine material. | m. | 15 | 0
| subtotal |  |  | 0
total fire alarm
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 70 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 4 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 2 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 12 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 4 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 4 | 0
Drip:
| KON 21; Rf 200212 | pieces | 4 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 4 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 10 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 10 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 5 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 5 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 90 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 80 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 20 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 45 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XI : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
VIII) | OUTDOOR LIGHTNING |  |  | 0
| CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
TOTAL OF ELE
TOTAL OF ELE+MECH

## B-06MECH
3. BILL OF QUANTITY-HYDRO (B-06)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
1.1. EARTHWORKS
1. PLUMBING
1.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
| Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x2. = |  |  | 0
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS |  |  |  | 0
1.2 | CONCRETE WORKS
1 | Making the connecting shafts of concrete, MB 20 in the corresponding panel. The size and shape of the detail. Perform treatment on walls and install creepers. | m3 | 1.1 | 0
1,2x1,2x0,35x1 + 0,8x0,75x1 =
TOTAL 1,2 CONCRETE WORKS
1.3. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
3 | Supply and installation of the cover size 80x80 with transport capacity of 25 tones. | psc | 1 | 0
Calculation per piece
TOTAL 1.3. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
1.4. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN50mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 21.81 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 10.23 | 0
Calculation per m of finished work
3 | Supply and installation of flat leaky ball valve Φ 2 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 1 | 0
Calculation per 1 pc. really built on the property.
4 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 3 | 0
Calculation per 1 pc. really built on the property.
5 | Supply and installation of ball valves with lever and unions Φ 1 " | psc | 3 | 0
Calculation per 1 pc. actually built the building
6 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 32.02 | 0
Calculation per m1 finished work.
TOTAL 1.4. ASSEMBLY WORK |  |  |  | 0
TOTAL 1. PLUMBING |  |  |  | 0
2. SPRINKLER NETWORK
2.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 2.1. EARTHWORKS |  |  |  | 0
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 2 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 1 | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for discharge line according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 10.8 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for line which is for emptying of sprinkler network according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 6.78 | 0
3 | Supply and installation of galvanized steel plumbing Φ 1 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 24.8 | 0
4 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN32mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 14.88 | 0
5 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN40mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 4.96 | 0
6 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 1.1 | 0
7 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 20.69 | 0
8 | Supply and installation of water pipes ducktail Ø 4"together with associated fittings. Calculation per m of finished work. | m1 | 8 | 0
9 | Supply and installation of water pipes ducktail Ø 8"together with associated fittings. Calculation per m of finished work. | m1 | 12 | 0
10 | Supply control valve for the dry signal system on Ø 3“. | psc | 3 | 0
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 3 | 0
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 3 | 0
13 | Supply of gate valve with oval body PN10 DN 80 | psc | 3 | 0
14 | Supply of gate valve with oval body PN10 DN 20 | psc | 1 | 0
15 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network.
|  | psc | 1 | 0
16 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 4.85 | 0
17 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | psc | 1 | 0
18 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector).
|  | psc | 1 | 0
19 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc. | 3 | 0
20 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1
| Calculation per m of finished work. |  | 107.26 | 0
TOTAL 2.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 2. SPRINKLER NETWORK |  |  |  | 0
3. PRECIPITATOR
3.1. | EARTHWORKS
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 31.24 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 18.72 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 15.02 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 2.68 | 0
| TOTAL EARTHWORKS |  |  | 0
3.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 1.08 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 3.86 | 0
3 | Fabrication and installation of armor for the bottom plate and walls. |  | 31.24 | 0
| MC 30 | Kg
| RA 400/500 | Kg
| TOTAL CONCRETE WORKS |  |  | 0
4.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 6 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | Psc | 2 | 0
| Dim. 80x90 cm | Psc | 2 | 0
| Dim. 80x95 | Psc | 2 | 0
3.3 | TOTAL ASSEMBLY WORK |  |  | 0
3 | TOTAL PRECIPITATOR |  |  | 0
RECAPITULATION
1. PLUMBING |  |  |  | 0
2.SPRINKLER NETWORK |  |  |  | 0
3.SEWAGE
4. PRECIPITATOR |  |  |  | 0
Total: |  |  |  | 0
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit KNNL d50 9/6-FM, FTT, RPDTA, KDTA, L, VF***9/6-A, FTT, RPDTA, L, VF (3420 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
- Section of plate recuperator with efficiency min 60% in summer period
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 3420 m3/h, the external pressure drop 500 Pa
-Flexible connection
Drain part:
-Flexible connection
Suction-section of vertical air intake
Section-filtration fabric filter class F5
- section of plate recuperator efficiency min. 60% in summer period
-Section of ventilator with direct drive, vertical discharge in »Ex« execution, flow with two values 3420 m3/h, external pressure drop 500 Pa
-Flexible connector
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 52oC
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 29,2 kW at evaporating temperature 5° and the outside temperature 46oC
- 15kW heating capacity at outside temperature 7oC
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
-elements of automation within the air chambers in the explosion-proof design
|  | set | 1 | 0
4 | -Equipment of the system for humidifying air. In all of the EMA as Hr.
-Pump Station high pressure
Condair HP100 with VFD capacity of water
5 ÷ 200 kg / h, N = 0.5 kW
| -Droplet eliminator Condair HP | Pcs | 1 | 0
size 600x300
| -System from the line with seven nozzles Condor HP capacity is 4.5 l / h | Pcs | 2 | 0
-Condor 3 HP, valve block of 3 valves with seven degrees of ventilation
| -HST 010 duct humidity sensor | Pcs | 2 | 0
-Condor HP Slave
| -Pipeline from f1/4'' | Pcs | 2 | 0
| Complete with commissioning | Pcs | 2 | 0
|  | Pcs | 2 | 0
|  | Pcs | 20 | 0
5 | Equipment for air distribution like of the Hidra Sl. in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 950x550
- exhaust exterior steel grate
Type AZR/ANŽ-4/3 size 950x550
- Diffuser for air supply with a box, model OD-11V/S/I19/Ex in plate 600x600mm
| size 315 | Pcs | 1 | 0
-air flow regulator MRP-1/Ex in front of OD-11/V
| Size 200 | Pcs | 1 | 0
- volume control damper RŽ-2/Ex-Z
| dim. 600x350 | Pcs | 4 | 0
- fire-damper wall width = 400
| PL-15 EL120S/A2/T12/Ex-Z | Pcs | 2 | 0
Size 500x350
| Size 300X350 | Pcs | 2 | 0
- Mounted box for the removal of air from the space type LN-3 from two strainer with filter F5 and manual control flow made ​​of stainless steel
height h = 2800, port f 250
|  | Pcs | 4 | 0
|  | Pcs | 4 | 0
|  | Pcs | 4 | 0
6 | Galvanized sheet metal ducts 1,00 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 900 | 0
7 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 150 | 0
8 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
| Total air conditioning equipment: |  |  | 0
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m | pcs
|  |  | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 30 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 10 | 0
5 | Delivery and installation of galvanized steel pipe T pieces- T piece 1/2"
|  | pcs | 5 | 0
6 | Supply and installation of valves for compressed air with connection for flexible hose.
- R 1/2"
|  | pcs | 4 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 3 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 10 | 0
9 | Small materials for bonding, rosette for pipes, etc. | all inclusive | 1 | 0
10 | Production of construction pipe penetrations 1/2 "through the wall (4 pcs.) finished with | All inclusive | 1 | 0
11 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
Total equipment for compressed air: |  |  |  | 0
Total of all(B-01)MECH |  |  |  | 462783.89
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_06"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_06. (See related scheme 1.4.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.K_6. (See related scheme 1.5.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
| TOTAL : |  |  | 0
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x50 mm2 (GRO -DO-TS) | m | 50 | 0
| XP00-A 4x35 mm2 | m | 25 | 0
| NHXH E60 4x25mm2 | m | 25 | 0
| PPOO 4x16mm2 | m | 10 | 0
| PPOO-Y 5x10 mm2 | m | 15 | 0
| PPOO-Y 5x2,5 mm2 | m | 10 | 0
| PPOO-Y 5x1,5 mm2 | m | 25 | 0
| PPOO-Y 3x2,5 mm2 | m | 18 | 0
| PPOO-Y 1x25 mm2 | m | 25 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 90 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 20 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 14 | 0
| PNK 200 | m | 20 | 0
| Slat cable carriers 200 mm | m | 20 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 10 | 0
3 | Other small material | flat | 1 | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 12 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 7 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 1 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 3 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 7 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 2 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 19 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 5 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 30 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 35 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0
| .serial water-proof n/ž | piece | 1 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 15 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 15 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 20 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 2 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 4 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 2 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 4 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 3 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 6 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 75 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 35 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 5 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm | m | 88 | 0
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 5 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 90 | 0
| -PP00-Y 3x2,5 mm2 | m. | 30 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 30 | 0
| - PVC warning tape | met | 30 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 3 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 3 | 0
3. | Protective canopy drip-channel for detector. | piece | 3 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 3 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 3 | 0
7. | Marking elements with persistent marks | piece | 3 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
TOTAL FLAME DETECTORS :
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 5 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 4 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 2 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 6 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 6 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
18. | Marking elements with persistent marks | piece | 6 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 3 | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0
6. | Marking elements with persistant marks | piece | 2 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 1 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 4 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0
9. | Other unspecified fine material. | m. | 15 | 0
| sub total |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
| . Handover and assembling the record on safety and functional testing. |  |  | 0
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 100 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 5 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 12 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 5 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 5 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 4 | 0
Drip:
| KON 21; Rf 200212 | pieces | 7 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 4 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 5 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 8 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 4 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 7 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 110 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 250 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 20 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 45 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE |  |  | 0
| CONNECTION TO TELEPHONE INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
TOTAL OF ELE
TOTAL OF ELE+MECH

## B-07-08 MECH
3. BILL OF QUANTITY-HYDRO (B-07-8)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
1.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work. 2x0,90x0,6+1.2x12.x12. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work.
2x0,60x0,2
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. (2,81-0,24) x 1,2
| TOTAL 1.1. EARTHWORKS |  |  | 0
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of RC structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | pcs | 0 | 0
Calculation per piece.
| TOTAL 1.2. MASONRY AND BRICKLAYERING WORK |  |  | 0
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1" (DN32mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1
| Calculation per m of finished work |  | 25.82 | 0
2 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | pcs
| Calculation per 1 pc. really built on the property. |  | 3 | 0
3 | Supply and installation of ball valves with lever and unions Φ 1 " | pcs
| Calculation per 1 pc. really built on the property. |  | 2 | 0
4 | Supply and installation of ready pipe 13mm thick polyurethane insulation for pipes Φ 1 "together with all the necessary papers and materials. | m1
| Calculation per m of finished work. |  | 25.82 | 0
5 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1
| Calculation per m1 finished work. |  | 52.82 | 0
TOTAL 1.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 1. PLUMBING |  |  |  | 0
2. SPRINKLER NETWORK
2.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV , along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trenchwith excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 2.1. EARTHWORKS |  |  |  | 0
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of RC structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0.001 | 0
Calculation per piece.
| TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  | 0
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 5.28 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the development of compounds for the exhaust valve signal line at the designs of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 12.06 | 0
3 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 36 | 0
4 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 36 | 0
5 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 18 | 0
6 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 9.6 | 0
7 | Supply and installation of water pipes ducktail Ø 4 "together with associated fittings. Calculation per m of finished work. | m1 | 7 | 0
8 | Supply and installation of water pipes ducktail Ø 6 "together with associated fittings. Calculation per m of finished work. | m1 | 12 | 0
9 | Supply and installation of water pipes ducktail Ø 8 "together with associated fittings. Calculation per m of finished work. | m1 | 8 | 0
10 | Supply control valve for the wet signal system on 3. " | pcs | 2 | 0
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | pcs | 2 | 0
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | pcs | 2 | 0
13 | Supply of gate valve with oval body PN10 DN 80 | pcs | 4 | 0
14 | Supply and installation of non-return valve Ø 6 „at the inlet line for sprinkler network.
|  | pcs | 2 | 0
15 | Supply and installation of non-return valve Ø 3 „at the inlet line for sprinkler network.
|  | pcs | 2 | 0
16 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 7.1 | 0
17 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | pcs | 1 | 0
18 | Supply and installation of connectors for connection Ø 3 fire engines "(double type connector).
|  | pcs | 1 | 0
19 | Supply and installation of flat leaky ball valve Φ 1 "in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property. | pcs | 2 | 0
20 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. Really built on the property. | pcs | 2 | 0
21 | Supply and installation of sprinkler Φ 1“, capacity 0, 69 l/s. | pcs
| Calculation per 1 pc. Really built on the property. |  | 96 | 0
23 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bars. | m1
| Calculation per m of finished work. |  | 143.9 | 0
TOTAL 2.3. ASSEMBLY WORK
| TOTAL 2. SPRINKLER NETWORK |  |  | 0
3. SEWAGE
Sewage consists of drains with grids that are processed in
architectural part of project.
REKAPITULATION
| 1. PLUMBING |  |  | 0
| 2. SPRINKLER NETWORK |  |  | 0
| TOTAL: |  |  | 0
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit like types: KNNL d50 12/9-FM, FTT, KDTA, L, VF (8500 m3/h) from Slovenia «Hidria» completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 100C /59% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 7400 m3 / h, the external pressure drop 500 Pa
-Flexible connection
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 80 kW at evaporating temperature and the outside temperature 50C to 460C
- 60kW heating capacity at outside temperature 0C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- Electric motor drives of dampers with spring return
|  | set | 1 | 0
4 | Roof radial fan in the anti-explosive performance as the Clima Celje, Slovenia.
types: EX SVK2-400/315-4/6,N=0,66/0,45 kW.
Some of the equipment cooling fan are:
- Flexible connector
- Auto -lift shutters
- Flange
- Supporting structure for the pitched roof in thermal protection
- Frequency regulator for speed control
|  | set | 2 | 0
5 | Axial fan as of Clima Celje Slovenia
AVS type EX 450-AP, n = 1400/min, N = 0.37 kW.
Some of the equipment cooling fan does
-Auto-lifting blinds
-Safety net
-Variable speed control speed
- Supporting structure and panels of 30 mm in the window pane
Standard place settings
|  | pcs | 4 | 0
6 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
Exterior steel grate with additional protection when working in touch with Saharan sand
APZR/ANŽ-4/3 types: size 1250x850
- Diffuser for air supply with a box, model
OD-11V/S/I19/Ex in the panel 600x600 mm
| size 250 | pcs | 1 | 0
- Air flow regulator MRP-1/Ex placed in front of the diffuser OD-11, f 200
| - Diffuser for air supply model OD-11V/Ex size 160 | pcs | 4 | 0
- Anti-fire dampers PL-15 EL120S/A2/T12/Ex-Z
| size 700x400 for wall width of L=750 | pcs | 4 | 0
size 400x250 for wall width of L=300
| -Mounted diffuser made ​​of stainless steel SD1/F1,H=1500,f 400 | pcs | 1 | 0
- Air flow regulator MRP-1/Ex placed in front of the diffuser size f 400
| -Grid on doors, from inox, size 350x350 | pcs | 1 | 0
| - Nozzle TŠ 5 / 400 | pcs | 1 | 0
- Setting shutter size 700x400
|  | pcs | 2 | 0
|  | pcs | 2 | 0
|  | pcs | 1 | 0
|  | pcs | 10 | 0
|  | pcs | 1 | 0
7 | Galvanized sheet metal ducts of square and circular diameter of plate 0.8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 360 | 0
8 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil - Ф 200
|  | m1 | 8 | 0
9 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 60 | 0
10 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
11 | Local air conditioning as of the LG Electronics
Internal unit:
AH 07 AH N40 (Qc/h=2,1/2,4 kW) kom.3
AH 09 AH N40 (Qc/h=2,5/2,9 kW) kom.1
External unit:
MU 5M 30 (Qc/h=8,8/10,1 kW) kom.1
Equipment for connection and commissioning.
| Set | set | 1 | 0
Total air conditioning equipment: |  |  |  | 0
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m
|  | set | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 30 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 10 | 0
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 4 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 2 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | kom | 2 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | kom | 6 | 0
9 | Small materials for bonding, rozetne of pipes, etc. | all inclusive | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
Total equipment for compressed air: |  |  |  | 0
Total of all(B-01)MECH |  |  |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | MAIN DISTRIBUTION CABINET "GRO-B7"
1 | Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks GRO-RO-B7. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet :
Section of grid voltage
1.2. | DISTRIBUTION CABINET "RO.B_7"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_7. (See related scheme 103.2.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
TOTAL :
II) | POWER CABLES |  |  | 0
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x95 mm2 (GRO -DO-TS) | m | 100 | 0
| NHXH E60 4x50mm2 | m | 30 | 0
| PPOO 4x16mm2 | m | 35 | 0
| PPOO-Y 5x16 mm2 | m | 18 | 0
| PPOO-Y 5x10 mm2 | m | 25 | 0
| PPOO-Y 5x6 mm2 | m | 14 | 0
| PPOO-Y 5x2,5 mm2 | m | 10 | 0
| PPOO-Y 5x1,5 mm2 | m | 25 | 0
| PPOO-Y 3x2,5 mm2 | m | 50 | 0
| PPOO-Y 1x70 mm2 | m | 36 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 150 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 10 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 20 | 0
| PNK 200 | m | 30 | 0
| PNK 300 | m | 45 | 0
| Slat cable carriers 200 mm | m | 30 | 0
| Slat cable carriers 300 mm | m | 45 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 28 | 0
3 | Other small material | flat | 1 | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 10 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 5 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 8 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 4 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 4 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 5 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 25 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 7 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 35 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 115 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 5 | 0
| .serial water-proof n/ž | piece | 5 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 2 | 0
| SKX 12/22 Serial switch SMS 03/8 - switch actuator SMO 17/5 - cable gland SPU 25, Type: SKX 12/22, TEP | piece | 2 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 20 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 5 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 50 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 3 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 8 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 7 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 10 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 3 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 120 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 3 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 3 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 130 | 0
| -PP00-Y 3x2,5 mm2 | m. | 22 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 125 | 0
| - PVC warning tape | met | 130 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 4 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 4 | 0
3. | Protective canopy drip-channel for detector. | piece | 4 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 4 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 4 | 0
7. | Marking elements with persistent marks | piece | 4 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
| TOTAL FLAME DETECTORS : |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 5 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 2 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 4 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 2 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 4 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 3 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 17 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 16 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
18. | Marking elements with persistent marks | piece | 16 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 3 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 3 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 3 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 3 | 0
6. | Marking elements with persistant marks | piece | 3 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 1 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 10 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 10 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 15 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 50 | 0
9. | Other unspecified fine material. | m. | 15 | 0
| sub total |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
| . Handover and assembling the record on safety and functional testing. |  |  | 0
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 60 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 4 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 6 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 30 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 8 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 8 | 0
Drip:
| KON 21; Rf 200212 | pieces | 8 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 9 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 8 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 30 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 4 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 60 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 110 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 80 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 80 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE |  |  | 0
| CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
TOTAL
TOTAL OF ELE+MECH

## B-09 MECH
3. BILL OF QUANTITY-HYDRO (B-09)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
1.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x2. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
| TOTAL 1.1. EARTHWORKS |  |  | 0
1.2. CONCRETE WORKS
1 | Making the connecting shafts of concrete, MB 20 in the corresponding panel. The size and shape of the detail. To carry out treatment on walls and install creepers. | m3 | 1.1 | 0
1,2x1,2x0,35x1 + 0,8x0,75x1 =
| 1.2. TOTAL CONCRETE WORKS |  |  | 0
1.3. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
3 | Supply and installation of cover 80x80 and transport capacity 25 tones | kom | 1 | 0
TOTAL 1.3. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
1.4. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN50mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 20.04 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 0 | 0
Calculation per m of finished work
3 | Supply and installation of flat leaky ball valve Φ 2" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 2 | 0
Calculation per 1 pc. really built on the property.
4 | Supply and installation of ball valves with lever and unions Φ 1 " | psc. | 1 | 0
Calculation per 1 pc. really built on the property.
5 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 20.04 | 0
Calculation per m1 finished work.
TOTAL 1.4. ASSEMBLY WORK |  |  |  | 0
2. SPRINKLER NETWORK
3.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 2,1. EARTHWORKS |  |  |  | 0
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for emptying of sprinkler network, together with the associated fittings. Calculation per m of finished work | m1 | 10.28 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for drain line near signal valve according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 3.25 | 0
3 | Supply and installation of steel galvanized water pipes Φ 1 "(DN25mm), with the connections, for cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 15.12 | 0
4 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN32mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 11.34 | 0
5 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN40mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 3.78 | 0
6 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 1.13 | 0
7 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 5.65 | 0
8 | Supply and installation of water pipes ducktail Ø 4"together with associated fittings. Calculation per m of finished work. | m1 | 19 | 0
9 | Supply and installation of DUCTIL water pipes Ø 8“ together with associated | m1 | 5 | 0
10 | Supply control valve for the dry signal system on Ø 3“. | psc | 1 | 0
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 1 | 0
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 1 | 0
13 | Supply of gate valve with oval body PN10 DN 80 | psc | 2 | 0
14 | Supply of gate valve with oval body PN10 DN 200 | psc | 1 | 0
15 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network.
|  | psc | 1 | 0
16 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 7.43 | 0
17 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | psc | 1 | 0
18 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector).
|  | psc | 1 | 0
19 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc. | 1 | 0
23 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 80.8 | 0
Calculation per m of finished work.
TOTAL 2.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 2. SPRINKLER NETWORK |  |  |  | 0
3. PRECIPITATOR
3.1. | EARTHWORKS
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 31.24 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 18.72 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 15.02 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 2.68 | 0
| TOTAL EARTHWORKS |  |  | 0
3.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 1.08 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 3.86 | 0
3 | Fabrication and installation of armor for the bottom plate and walls. |  | 31.24 | 0
| MC 30 | Kg
| RA 400/500 | Kg
| TOTAL CONCRETE WORKS |  |  | 0
3.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 6 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | Psc | 2 | 0
| Dim. 80x90 cm | Psc | 2 | 0
| Dim. 80x95 | Psc | 2 | 0
3.3 | TOTAL ASSEMBLY WORK |  |  | 0
3 | TOTAL PRECIPITATOR |  |  | 0
RECAPITULATION
| 1. PLUMBING |  |  | 0
| 2.SPRINKLER NETWORK |  |  | 0
3.SEWAGE
| 4. PRECIPITATOR |  |  | 0
| Total: |  |  | 0
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit type KNNL d50 6/5-FM, FTT, KD, BD, L, VF (950 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
Section of the steam moisturizer with steam generator 20 kg / h
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 950 m3 / h, the external pressure drop 500 Pa
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 20,0 kW at evaporating temperature 5° and the outside temperature 460C
- 15kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
-elements of automation within the air chambers in the explosion-proof design
|  | set | 1 | 0
4 | -Radial channel fan
| CA 20VD Ex,N=18 kW | pcs | 2 | 0
-External protective grid made from stainless steel with self raising with jalousies f 200
| -Control unit of radial fan with air flow regulation | pcs | 2 | 0
| -Suction grid with flow regulation size 250x400 | pcs | 2 | 0
|  | pcs | 2 | 0
5 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 650x450
-diffuser air intake with a box model
OD-11V/S/I19/Ex the panel 600x600 mm
size 250
| -Air-flow regulator MRP-1/Ex placed ahead of 11 | pcs | 1 | 0
size 160
| -fire-damper wall width L = 500 | pcs | 3 | 0
PL-15 EL120S/A2/T12/Ex-Z
| dim.500x250 | pcs | 3 | 0
|  | pcs | 1 | 0
6 | Galvanized sheet metal ducts 0.80 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 200 | 0
7 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 30 | 0
7 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
Total air conditioning equipment: |  |  |  | 0
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m | pcs
|  |  | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 12 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
|  | pcs | 6 | 0
5 | Delivery and installation of galvanized steel pipe T pieces- T piece 1/2"
|  | pcs | 2 | 0
6 | Supply and installation of valves for compressed air with connection for flexible hose.
- R 1/2"
|  | pcs | 2 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 1 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 5 | 0
9 | Small materials for bonding, rosette for pipes, etc. | all inclusive | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
Total equipment for compressed air: |  |  |  | 0
Total of all(B-01)MECH |  |  |  | 302507.87
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_09"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_09. (See related scheme 1.4.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
| TOTAL : |  |  | 0
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x35 mm2 (GRO -DO-TS) | m | 50 | 0
| NHXH E60 4x6mm2 | m | 20 | 0
| PPOO 4x16mm2 | m | 15 | 0
| PPOO-Y 5x4 mm2 | m | 10 | 0
| PPOO-Y 5x2,5 mm2 | m | 10 | 0
| PPOO-Y 5x1,5 mm2 | m | 25 | 0
| PPOO-Y 3x2,5 mm2 | m | 25 | 0
| PPOO-Y 1x25 mm2 | m | 25 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 45 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 20 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0
| PNK 200 | m | 17 | 0
| Slat cable carriers 200 mm | m | 17 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 25 | 0
3 | Other small material | flat | 1 | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 16 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 9 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 1 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 5 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 10 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 2 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 36 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 7 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 30 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 45 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0
| .serial water-proof n/ž | piece | 1 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 6 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 3 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 45 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 50 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 3 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 30 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 2 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 4 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 2 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 5 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 5 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 6 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 110 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 10 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm | m | 120 | 0
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 4 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 120 | 0
| -PP00-Y 3x2,5 mm2 | m. | 25 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 30 | 0
| - PVC warning tape | met | 30 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 4 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 4 | 0
3. | Protective canopy drip-channel for detector. | piece | 4 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 3 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 3 | 0
7. | Marking elements with persistent marks | piece | 3 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
| TOTAL FLAME DETECTORS : |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 7 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 4 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 2 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 3 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 3 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 15 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 6 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 6 | 0
18. | Marking elements with persistent marks | piece | 6 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 3 | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0
6. | Marking elements with persistant marks | piece | 2 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 1 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 4 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0
9. | Other unspecified fine material. | m. | 15 | 0
| SUB TOTAL |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
| . Handover and assembling the record on safety and functional testing. |  |  | 0
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 140 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 3 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 2 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 4 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 3 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 3 | 0
Drip:
| KON 21; Rf 200212 | pieces | 5 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 2 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 5 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 6 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 7 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 7 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 190 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 50 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 9 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 30 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
VIII) | OUTDOOR LIGHTNING |  |  | 0
| CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
TOTAL OF ELE
TOTAL OF ELE+MECH

## B-10 MECH
3. BILL OF QUANTITY-HYDRO (B-10)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
1.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work. 2x0,90x0,6+1.2x12.x12. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work. 2x0,60x0,2
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work (2,81-0,24) x 1,2
| TOTAL 1.1. EARTHWORKS |  |  | 0
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0
Calculation per piece.
| TOTAL 1.2. MASONRY AND BRICKLAYERING WORK |  |  | 0
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 26.44 | 0
Calculation per m of finished work
2 | Supply and installation of flat leaky ball valve Φ 1" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | pcs | 2 | 0
Calculation per 1 pc. really built on the property.
3 | Supply and installation of ball valves with lever and unions Φ 1 " | pcs | 1 | 0
Calculation per 1 pc. really built on the property.
4 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 26.44 | 0
Calculation per m1 finished work.
TOTAL 1.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 1. PLUMBING PIPELINE |  |  |  | 0
2. SPRINKLERS NETWORK
2.1. EARTHWORKS
The calculation is performed by plumbing works, because the installation of water and hydrant network laid in the same trench.
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3
Calculation per m3 of finished work
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3of finished work.
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1
Calculation per m3of finished work.
| TOTAL 2.1. EARTHWORKS |  |  | 0
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
| TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  | 0
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1" (DN32mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 2.98 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ | m1
| " (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. |  | 18 | 0
Calculation per m of finished work.
3 | Supply and installation of steel galvanized water pipes Φ | m1
| " (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. |  | 16 | 0
Calculation per m of finished work.
4 | Supply and installation of steel galvanized water pipes Φ 2" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 20 | 0
Calculation per m of finished work.
5 | Supply and installation of steel galvanized water pipes Φ 3" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 4 | 0
Calculation per m of finished work.
6 | Supply and installation of ducktil water pipes Φ 4" together with associated fittings. | m1 | 20 | 0
| Calculation per m1 of finished work. |  | 20 | 0
7 | Supply of control signal valve for wet system Ø 4“. | pcs | 1 | 0
8 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | pcs | 1 | 0
9 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | pcs | 1 | 0
10 | Supply of gate valve with oval body PN10 DN 100 | psc | 2 | 0
GATE VALVE WITH OVAL BODY
11 | Supply and installation of non-return valve diameter 4 " at the inlet line for sprinkler network.
|  | psc | 1 | 0
12 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 5.82 | 0
13 | Supply and installation of non-return valve Ø 3” at the inlet lines for fire trucks.
|  | psc | 1 | 0
14 | Supply and installation of connectors for connection Ø 3 fire engines "(double type connector).
|  | psc | 1 | 0
15 | Supply and installation of flat leaky ball valve Φ 1" in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property. | psc | 1 | 0
16 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. Really built on the property. | psc | 1 | 0
17 | Supply and installation of sprinkler Φ1" with capacity of 0,93 l/s. Calculation per 1 pc. Really built on the property. | psc | 44 | 0
18 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 111.1 | 0
Calculation per m of finished work
| TOTAL 2.3. ASSEMBLY WORK |  |  | 0
| TOTAL 2. SPRINKLER NETWORK |  |  | 0
3. SEWAGE
EARTHWORKS
1 | Excavation of earth categorie III mechanical way at a depth of 0-3.5 m with rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 15.62 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 9.36 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. (15,62 – 9,36)x1,20 | m3 | 7.51 | 0
4 | Supply, filling and compacting gravel for the bottom plate surface at a thickness of septi 20 cm | m3 | 1.34 | 0
| TOTAL EARTHWORKS |  |  | 0
3.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 0.54 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 1.93 | 0
3 | Fabrication and installation of armor for the bottom plate and walls.
| MC 30 | Kg
| RA 400/500 | Kg
| TOTAL CONCRETE WORKS |  |  | 0
3.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | psc | 3 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | psc | 1 | 0
| Dim. 80x90 cm | psc | 1 | 0
| Dim. 80x95 | psc | 1 | 0
TOTAL ASSEMBLY WORK |  |  |  | 0
3 | TOTAL SEWAGE |  |  | 0
RECAPITULATION
1. PLUMBING |  |  |  | 0
2.SPRINKLER NETWORK |  |  |  | 0
3.SEWAGE |  |  |  | 0
| Total: |  |  | 0
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit like types: KNNL d50 6/6-FM, FTT, EW, BD, L, VF (2100 m3/h) from «Hidria» Slovenia completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 700C
-Winter-design conditions:
Outdoor air: 60C /59% r.v., space 700C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 700C in summer
-section of steam humidifier with steam generator of 20 kg/h o exit min. 70%
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 2100 m3 / h, the external pressure drop 500 Pa
|  | pcs | 1 | 0
2 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
- Automatic elements inside the air conditioning chambers in anti-explosive performance
|  | pcs | 1 | 0
3 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
APZR/ANŽ-4/3 types: size 650x550
- Diffuser for air supply with a box, model
OD-11V/S/I19/Ex in the panel 600x600 mm
| size 200 | pcs | 1 | 0
- Air flow regulator MRP-1/Ex placed in front of the diffuser OD-11 size 160
- Fire damper wall width L=500
| PL-15 EL120S/A2/T12/Ex-Z | pcs | 7 | 0
Size 500x250
- External inox grid with protective inox network and auto-lifting blinds from aluminium sheet metal, size 500x300
|  | pcs | 7 | 0
|  | pcs | 1 | 0
|  | pcs | 4 | 0
4 | Insulation of sheet metal part of channel outside the object with hard mineral wool of 100 mm coated in inox sheet metal 0.88 mm
Calculated per m2
|  | m2 | 6 | 0
5 | Galvanized sheet metal ducts of square and circular diameter of plate 0.8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 250 | 0
6 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil- f 160
|  |  | 20 | 0
7 | Insulation of sheet metal part of channel outside the object with hard mineral wool of 100 mm coated in inox sheet metal
|  | m2 | 6 | 0
8 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 40 | 0
9 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
Total equipment for air conditioning: |  |  |  | 0
No | An item of bill of quantities –heat substation- delivery, transportation, assembly- | Unit of measure | Quantity | Total price
11 | Heat substation
Fin heat exchanger of 100 kW
- Primary side water 130/900C, dp = 2000P
- Secondary side water 90/700C, dp = 1500pa
Armour of substation
Valve with unions NP16
- R-1'', 2 pcs
-R-5/4'', 2 pcs
-Fill & drain R ½'' kom.2
Control circuit hot water
-regulating circuit,
- Electric line valve R 1'',
- Limit thermostat 900C,
- Initial temperature sensor,
- sensor for initial temperature of air conditioning air
- Spatial sensor
- Circulation pump Wilo
Star RS 25/8, N = 0.157 kW
- Expansion vessel shut V = 15 lit with sig. valve R1/2''
- Pressure gauge 0-6 bar,
- Pressure gauge 0-16 bar,
- Thermometer 0-1200C AM,
- Thermometer 0-1800C,
- Connecting a secondary piping F1'' length l = 6m
set
| Note: the primary pipeline is not subject of bill of quantities (provided by the investor | set | 1 | 0
| Total heat substation: |  |  | 0
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m
|  | set | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 18 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 8 | 0
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 2 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 1 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 1 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 5 | 0
9 | Small materials for bonding, rozetne of pipes, etc. | all inclusive | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
Total equipment for compressed air: |  |  |  | 0
TOTAL OF MECH |  |  |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_10"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_10. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
| TOTAL : |  |  | 0
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x95 mm2 (GRO -DO-TS) | m | 100 | 0
| PPOO 4x35mm2 | m | 25 | 0
| PPOO-Y 5x16 mm2 | m | 15 | 0
| PPOO-Y 5x2,5 mm2 | m | 10 | 0
| PPOO-Y 3x2,5 mm2 | m | 20 | 0
| PPOO-Y 1x35 mm2 | m | 25 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 100 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 7 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0
| PNK 200 | m | 30 | 0
| PNK 300 | m | 20 | 0
| Slat cable carriers 200 mm | m | 30 | 0
| Slat cable carriers 300 mm | m | 20 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 15 | 0
3 | Other small material | flat | 1 | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The floodlight is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air.Hazardous zones: 1,2, 21, 22. Housing: aluminium powder painted casting Diffuser: borosilicate tube glass, IP 66 in accordance with EN 60529+A1, category 1, RLF/250 HST, 250 W Accessories: protected galvanized steel gird, assembly kit for wall, pipe and ceiling mounting Ex de IIC T4-T3 or Ex d IIC T4-T3 tD A21 IP66 T10ºC-150ºC, 231V, 60 Hz, | piece | 2 | 0
2. | The floodlight is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air.Hazardous zones: 1,2, 21, 22. Housing: aluminium powder painted casting Diffuser: borosilicate tube glass, IP 66 in accordance with EN 60529+A1, category 1, RLF/85 QL, 85 W Accessories: protected galvanized steel gird, assembly kit for wall, pipe and ceiling mounting Ex de IIC T4-T3 or Ex d IIC T4-T3 tD A21 IP66 T10ºC-150ºC, 231V, 60 Hz, | piece | 2 | 0
3. | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 3 | 0
5. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 1 | 0
6. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 1 | 0
7. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 1 | 0
8. | Other unspecified material needed for the installation | kpl | 1 | 0
9. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 14 meters. | piece | 7 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 3 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 20 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 30 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0
| .serial water-proof n/ž | piece | 1 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 2 | 0
| SKX 12/22 Serial switch SMS 03/8 - switch actuator SMO 17/5 - cable gland SPU 25, Type: SKX 12/22, TEP | piece | 1 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 11 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 5 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 20 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 1 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 1 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 2 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 10 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 10 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | m | 3 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 1 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 170 | 0
| -PP00-Y 3x2,5 mm2 | m. | 37 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 150 | 0
| - PVC warning tape | met | 150 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version. | piece | 2 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 2 | 0
3. | Protective canopy drip-channel for detector. | piece | 2 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
7. | Marking elements with persistent marks | piece | 2 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
| TOTAL FLAME DETECTORS : |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 3 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
| Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 1 | 0
3 | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0
4 | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-, II 2 G Ex ib IIC T4,IP-54SECURITON | piece | 1 | 0
5 | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 1 | 0
6 | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 5 | 0
7. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
8. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
9. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 9 | 0
10. | Supply and delivery of mark elements for the fire alarm system | piece | 9 | 0
11. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
12. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
13. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
14. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
15. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
16. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
17. | Marking elements with persistent marks | piece | 16 | 0
18. | Other unspecified fine material. | kpl. | 1 | 0
19. | Installation and connection of the detector, all the EX version. | kpl. | 1 | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0
6. | Marking elements with persistant marks | piece | 1 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 2 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 2 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 2 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
· 1 piece of the Power supply unit 24V, 5A,
· 1 piece of the rechargeable battery 2x12V, 7,2Ah,
· 1 piece of the automatic fuse 6A,
· relay vard with three relays 24V/2A
· 40 pieces of Two-stairs VS terminals 1.5mm2,
· spaces for safety barriers
· spaces for MDI module
· spaces for SOM module
· 1 piece of the. DIN šina,
· perforated tiles with lid
· other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 5 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 3 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 5 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 5 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0
9. | Other unspecified fine material. | m. | 15 | 0
| SUB TOTAL |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 70 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 4 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 2 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 12 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 4 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 4 | 0
Drip:
| KON 21; Rf 200212 | pieces | 4 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 4 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 10 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 10 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 5 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 5 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 90 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 80 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 20 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 45 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XI : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
| OUTDOOR LIGHTNING |  |  | 0
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
TOTAL OF ELE
TOTAL OF ELE+MECH

## B-11MECH
3. BILL OF QUANTITY-HYDRO (B-11)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work.
2x0,90x0,6+1.2x12.x12. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work.
2x0,60x0,2
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. (2,81-0,24) x 1,2
TOTAL 1.1. EARTHWORKS |  |  |  | 0
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of RC structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 1.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 25.82 | 0
Calculation per m of finished work
2 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | pcs | 3 | 0
Calculation per 1 pc. really built on the property.
3 | Supply and installation of ball valves with lever and unions Φ 1 " | pcs | 2 | 0
Calculation per 1 pc. really built on the property.
4 | Supply and installation of completed pipe with 13mm thick polyurethane insulation for pipes Φ 1 "together with all necessary papers and materials. | m1 | 25.82 | 0
Calculation per m1 finished work.
5 | Testing od installation by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 51.64 | 0
Calculation per m1 finished work.
TOTAL 1.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 1. PLUMBING |  |  |  | 0
2. SPRINKLER NETWORK
2.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV , along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
| TOTAL 2.1. EARTHWORKS |  |  | 0
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of RC structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
| TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  | 0
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 41.28 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the development of compounds for the exhaust valve signal line at the designs of the project, together with the associated fittings.. Calculation per m of finished work. | m1 | 9.18 | 0
3 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings .Calculation per m of finished work. | m1 | 36 | 0
4 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 54 | 0
5 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 3.2 | 0
6 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 14.4 | 0
7 | Supply and installation of water pipes ducktail Ø 4 "together with associated fittings. Calculation per m of finished work. | m1 | 26.88 | 0
| Supply of control valve for the wet signal system Ø 4“. | pcs | 2 | 0
8 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | pcs | 2 | 0
9 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | pcs | 2 | 0
10 | Supply of gate valve with oval body PN10 DN 80 | pcs | 2 | 0
11 | Supply and installation of non-return valve Ø 4 at the inlet line for sprinkler network. |  |  | 0
0
|  | pcs | 2 | 0
12 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 2.3 | 0
13 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | pcs | 1 | 0
14 | Supply and installation of connectors for connection Ø 3" fire engines (double type connector). |  |  | 0
0
|  | pcs | 1 | 0
15 | Supply and installation of flat leaky ball valve Φ 1 "in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property. | pcs | 2 | 0
16 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. really built on the property. | pcs | 2 | 0
17 | Supply and installation of sprinkler Φ1 "Calculation per 1 pc. really built on the property. | pcs | 96 | 0
18 | Supply and installation of ready pipe 13mm thick polyurethane insulation for pipes Φ 1 " together with all the necessary papers and materials. | m1
Calculation per m1 finished work.
19 | Supply and installation of ready pipe 13mm thick polyurethane insulation for pipes Φ 5/4 " along with all necessary papers and materials. | m1
Calculation per m1 finished work.
20 | Supply and installation of ready pipe 13mm thick polyurethane insulation for pipes Φ 2 " along with all necessary papers and materials. Calculation per m1 finished work. | m1
21 | Supply and installation of ready pipe 13mm thick polyurethane insulation for pipes Φ 3 " along with all necessary papers and materials. Calculation per m1 finished work. | m1
22 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 175.76 | 0
Calculation per m of finished work.
TOTAL 2.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 2. SPRINKLER NETWORK |  |  |  | 0
3. SEWAGE
Sewage consists of drains with grates that are processed in
the architectural part of the project.
REKAPITULATION
1. PLUMBING |  |  |  | 0
2 SPRINKLER NETWORK |  |  |  | 0
TOTAL: |  |  |  | 0
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit like types: KNND d50 9/6-FM, FTT, RPDTA, KD, BD, L, VF***9/6 – A, FTT, RPDTA, L,VF (4100 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /59% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
- Section of steam humifider with steam generator 20 kg/h
-Empty sections
-Section-fan, direct drive, vertical discharge, flow with two values 4100/2150 m3 / h, the external pressure drop 500 Pa
-Flexible connection
-Drainage section:
-Flexible connection
- Intake section for vertical input of air
- section of baggy filter filtration class F5
- section of plate recuperator efficiency min. 60% in summer period
- section of ventilators in anti explosive Ex performance with direct drive, vertical blowing, flow 4100/2150 m3/h,external pressure drop 500 Pa
- blinds of waste air
- flexible connector
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- Cooling capacity of 32 kW at evaporating temperature and the outside temperature 50C to 460C
- 25kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber Cu pipes f 12,7/22 (met.20) .
|  | pcs | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
|  | pcs | 1 | 0
4 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
- Exterior steel grate with additional protection when working in touch with Saharan sand
Type APZR/ANŽ-4/3 size 950x550
-Exhaust exterior inox grid
Type AZR/ANŽ-4/3 size 950x550
- Diffuser model OD-11V/P/KR/I19/Ex/I19 in the panel 600x600 mm
| size 200 | pcs | 1 | 0
- air flow regulator MRP-1/Ex placed in front of OD 11/V
| size 160 | pcs | 1 | 0
-fire damper for wall L=200 mm
PL-15 EL120S/A2/T12/Ex-Z
| dim.400x200 | pcs | 12 | 0
dim.500x350
Pillar box is made of stainless steel for the removal of air from the space type LN-3 from two strainer with filter F5 and manual control flow
| -height h = 2800, port f 250 | pcs | 12 | 0
|  | pcs | 2 | 0
|  | pcs | 2 | 0
|  | pcs | 4 | 0
5 | Sheet metal ducts of galvanized sheet 1.0 mm with sealing, connection production, supplies for hanging, opened for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 500 | 0
6 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
f 160
f 250
|  | m | 50 | 0
|  | m | 40 | 0
7 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 80 | 0
8 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
Total air conditioning equipment: |  |  |  | 0
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m
|  | set | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 24 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 6 | 0
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 3 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 3 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | kom | 2 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | kom | 8 | 0
9 | Small materials for bonding, rozetne of pipes, etc. | all inclusive | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
Total equipment for compressed air: |  |  |  | 0
| TOTAL OF MECH |  |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_11"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_11. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0 | 0
| TOTAL : |  |  | 0
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x50 mm2 (GRO -DO-TS) | m | 100 | 0 | 0
| NHXH E60 4x35mm2 | m | 30 | 0 | 0
| PPOO 4x16mm2 | m | 15 | 0 | 0
| PPOO-Y 5x10 mm2 | m | 13 | 0 | 0
| PPOO-Y 5x4 mm2 | m | 14 | 0 | 0
| PPOO-Y 5x2,5 mm2 | m | 5 | 0 | 0
| PPOO-Y 5x1,5 mm2 | m | 15 | 0 | 0
| PPOO-Y 3x2,5 mm2 | m | 5 | 0 | 0
| PPOO-Y 1x35 mm2 | m | 30 | 0 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 50 | 0 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 5 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0 | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0 | 0
| PNK 200 | m | 20 | 0 | 0
| PNK 300 | m | 25 | 0 | 0
| Slat cable carriers 200 mm | m | 20 | 0 | 0
| Slat cable carriers 300 mm | m | 25 | 0 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 15 | 0 | 0
3 | Other small material | flat | 1 | 0 | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 18 | 0 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 3 | 0 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 4 | 0 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 2 | 0 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 2 | 0 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 2 | 0 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0 | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 24 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 4 | 0 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 35 | 0 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 60 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0 | 0
| .serial water-proof n/ž | piece | 3 | 0 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0 | 0
| SKX 12/22 Serial switch SMS 03/8 - switch actuator SMO 17/5 - cable gland SPU 25, Type: SKX 12/22, TEP | piece | 1 | 0 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 2 | 0 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 2 | 0 | 0
11 | Other small material | flat | 1 | 0 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 20 | 0 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 5 | 0 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 50 | 0 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 3 | 0 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0 | 0
8. | Other small material | flat | 1 | 0 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0
TOTAL VI: |  |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 4 | 0 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 10 | 0 | 0
6 | Creating bypass Gauge | piece | 1 | 0 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0 | 0
8 | Testing of installed installations | pšl | 1 | 0 | 0
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 4 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 90 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 4 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 110 | 0 | 0
| -PP00-Y 3x2,5 mm2 | m. | 25 | 0 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 100 | 0 | 0
| - PVC warning tape | met | 100 | 0 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0 | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 4 | 0 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 4 | 0 | 0
3. | Protective canopy drip-channel for detector. | piece | 4 | 0 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 4 | 0 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 4 | 0 | 0
7. | Marking elements with persistent marks | piece | 4 | 0 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | 0
| TOTAL FLAME DETECTORS : |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 3 | 0 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 2 | 0 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 2 | 0 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 4 | 0 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 17 | 0 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 16 | 0 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0 | 0
18. | Marking elements with persistent marks | piece | 10 | 0 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0 | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0 | 0
6. | Marking elements with persistant marks | piece | 2 | 0 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0 | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0 | 0
5. | Marking elements with persistant marks | piece | 1 | 0 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0 | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0 | 0
| Cabinet includes: | piece | 1 | 0 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0 | 0
4. | Marking elements with persistent marks | piece | 2 | 0 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 7 | 0 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 7 | 0 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 35 | 0 | 0
9. | Other unspecified fine material. | m. | 15 | 0 | 0
| SUB TOTAL |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
| . Handover and assembling the record on safety and functional testing. |  |  | 0 | 0
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 80 | 0 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 4 | 0 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 2 | 0 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 8 | 0 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 4 | 0 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 4 | 0 | 0
Drip:
| KON 21; Rf 200212 | pieces | 4 | 0 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 3 | 0 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 4 | 0 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 30 | 0 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 7 | 0 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 7 | 0 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 80 | 0 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 200 | 0 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 25 | 0 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 45 | 0 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
| OUTDOOR LIGHTNING |  |  | 0
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
TOTAL OF ELE
TOTAL OF ELE+MECH

## B-12-15 MECH
3. BILL OF QUANTITY-HYDRO (B-12-15)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work.
2x0,90x0,6+1.2x12.x12. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work.
2x0,60x0,2
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. (2,81-0,24) x 1,2
| TOTAL 1.1. EARTHWORKS |  |  | 0
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of RC structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0
Calculation per piece.
| TOTAL 1.2. MASONRY AND BRICKLAYERING WORK |  |  | 0
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 17.65 | 0
Calculation per m of finished work
2 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | pcs | 2 | 0
Calculation per 1 pc. really built on the property.
3 | Supply and installation of ball valves with lever and unions Φ 1 " | pcs | 1 | 0
Calculation per 1 pc. really built on the property.
4 | Supply and installation of completed pipe with 13mm thick polyurethane insulation for pipes Φ 1 "together with all necessary papers and materials. | m1 | 17.65 | 0
Calculation per m1 finished work.
5 | Testing od installation by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 17.65 | 0
Calculation per m1 finished work.
TOTAL 1.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 1. PLUMBING |  |  |  | 0
2. SPRINKLER NETWORK
2.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV , along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
| Calculation per m3 of finished work. |  |  | 0
TOTAL 2.1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of RC structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 2 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
| Calculation per piece. |  |  | 0
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 2.51 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the development of compounds for the exhaust valve signal line at the designs of the project, together with the associated fittings.. Calculation per m of finished work. | m1 | 4.63 | 0
3 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings .Calculation per m of finished work. | m1 | 8.1 | 0
4 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 1.55 | 0
5 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 9.71 | 0
6 | Supply and installation of water pipes ducktail Ø 4 "together with associated fittings. Calculation per m of finished work. | m1 | 10 | 0
7 | Supply of control valve for the wet signal system Ø 4“. | pcs | 1 | 0
8 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | pcs | 1 | 0
9 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | pcs | 1 | 0
10 | Supply of gate valve with oval body PN10 DN 80 | pcs | 2 | 0
11 | Supply and installation of non-return valve Ø 4 at the inlet line for sprinkler network.
|  | pcs | 1 | 0
12 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 2.3 | 0
13 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | pcs | 1 | 0
14 | Supply and installation of connectors for connection Ø 3" fire engines (double type connector).
|  | pcs | 1 | 0
15 | Supply and installation of flat leaky ball valve Φ 1 "in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property. | pcs | 3 | 0
16 | Supply and installation of ball valves with lever and unions Φ 1 " Calculation per 1 pc. really built on the property. | pcs | 2 | 0
17 | Supply and installation of sprinkler Φ1 " with capacity of 0,62l/s Calculation per 1 pc. really built on the property. | pcs | 24 | 0
18 | Supply and installation of ready pipe 13mm thick polyurethane insulation for pipes Φ 1 " together with all the necessary papers and materials. | m1
Calculation per m1 finished work.
19 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 31.89 | 0
Calculation per m of finished work.
TOTAL 2.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 2. SPRINKLER NETWORK |  |  |  | 0
3. SEWAGE
Sewage consists of drains with grates that are processed in
the architectural part of the project.
REKAPITULATION
1. PLUMBING |  |  |  | 0
2 SPRINKLER NETWORK |  |  |  | 0
TOTAL: |  |  |  | 0
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit like type KNND d50 6/5-FM, FTT, RPDTA, KD, BD, L, VF***6/5 – A, FTT, RPDTA, L,VF (900 m3/h) product of Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 6oC/80% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-section of plate recuperator eficiency 60% min, in summer period
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
-Section-steam humidifiers with steam generator 20 kg / h,
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 900 m3 / h, the external pressure drop 300 Pa
-Flexible connection
- Air exhaust part:
-Flexible connection
- Intake section for vertical air intake
- Section of bag filter class F5
- Section of plate recuperator efficiency 60% min, in summer period
- Section-fan anti explosive Ex performance, direct drive, vertical discharge, flow of 900 m3 / h, the external pressure drop 300 Pa
- Exhaust air dampers
- Flexible connection
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 10.9 kW at evaporating temperature and the outside temperature 50C to 460C
- 8 kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
|  | set | 1 | 0
4 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
- exterior steel grate with additional protection when working in touch with Saharan sand type APZR/ANŽ-4/3 size 600X450
- exterior exhaust grille of stainless steel type AZR/ANŽ-4/3 size 600X450
- Diffuser model OD-11V/P/KR/I19/Ex/I19 in a panel 600x600 mm
veličina 200
-air flow regulator MRP-1/Ex in front of OD-11/V size160
| - Fire damper for wall width L=300 | pcs | 1 | 0
PL-15 EL120S/A2/T12/Ex-Z
| Size 400x200 | pcs | 1 | 0
Pillar box made from stainless steel for removal of air from the room, type LN-3 from two strainers with filter F5 and manual control flow-height h = 2800mm, connector f 250
|  | pcs | 4 | 0
|  | pcs | 4 | 0
|  | pcs | 2 | 0
|  | pcs | 2 | 0
5 | Galvanized sheet metal ducts of square and circular diameter of plate 0.8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 250 | 0
6 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
f 160
f 250
|  | m | 20 | 0
|  | m | 10 | 0
7 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 40 | 0
8 | Fine regulation, commissioning, testing capacity and quantity.
Total air conditioning equipment: |  |  |  | 0
| TOTAL OF MECH |  |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_12"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_12. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
| TOTAL : |  |  | 0
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x50 mm2 (GRO -DO-TS) | m | 100 | 0
| NHXH E60 4x35mm2 | m | 30 | 0
| PPOO 4x16mm2 | m | 15 | 0
| PPOO-Y 5x10 mm2 | m | 13 | 0
| PPOO-Y 5x4 mm2 | m | 14 | 0
| PPOO-Y 5x2,5 mm2 | m | 5 | 0
| PPOO-Y 5x1,5 mm2 | m | 10 | 0
| PPOO-Y 3x2,5 mm2 | m | 5 | 0
| PPOO-Y 1x35 mm2 | m | 30 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 25 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 5 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0
| PNK 200 | m | 20 | 0
| PNK 300 | m | 10 | 0
| Slat cable carriers 200 mm | m | 20 | 0
| Slat cable carriers 300 mm | m | 10 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 10 | 0
3 | Other small material | flat | 1 | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 6 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 2 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 1 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 1 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 1 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 1 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 10 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 4 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 20 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 33 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0
| .serial water-proof n/ž | piece | 1 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 14 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 5 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 35 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 3 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 3 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 4 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 8 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 3 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 70 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 4 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 70 | 0
| -PP00-Y 3x2,5 mm2 | m. | 18 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 80 | 0
| - PVC warning tape | met | 80 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 2 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 2 | 0
3. | Protective canopy drip-channel for detector. | piece | 2 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
7. | Marking elements with persistent marks | piece | 2 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
| TOTAL FLAME DETECTORS : |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 2 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 10 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 7 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
18. | Marking elements with persistent marks | piece | 7 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0
6. | Marking elements with persistant marks | piece | 2 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 1 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 4 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 6 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box |  |  | 0
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 15 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 15 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 15 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0
9. | Other unspecified fine material. | m. | 15 | 0
| SUB TOTAL |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
| . Handover and assembling the record on safety and functional testing. |  |  | 0
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 130 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 2 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 2 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 6 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 2 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 2 | 0
Drip:
| KON 21; Rf 200212 | pieces | 4 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 2 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 4 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 20 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 4 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 3 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 45 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 45 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 40 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 25 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
TOTAL OF ELE
TOTAL OF ELE+MECH

## B-13 MECH
3. BILL OF QUANTITY-HYDRO (B-13)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work.
2x0,90x0,6+1.2x12.x12. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work.
2x0,60x0,2
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. (2,81-0,24) x 1,2
TOTAL 1.1. EARTHWORKS |  |  |  | 0
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of RC structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 1.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 25.82 | 0
Calculation per m of finished work
2 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | pcs | 3 | 0
Calculation per 1 pc. really built on the property.
3 | Supply and installation of ball valves with lever and unions Φ 1 " | pcs | 2 | 0
Calculation per 1 pc. really built on the property.
4 | Supply and installation of completed pipe with 13mm thick polyurethane insulation for pipes Φ 1 "together with all necessary papers and materials. | m1 | 25.82 | 0
Calculation per m1 finished work.
5 | Testing of installation by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 25.82 | 0
Calculation per m1 finished work.
TOTAL 1.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 1. PLUMBING |  |  |  | 0
2. SPRINKLER NETWORK
2.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV , along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
| TOTAL 2.1. EARTHWORKS |  |  | 0
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of RC structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
| Calculation per piece. |  |  | 0
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 41.28 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the development of compounds for the exhaust valve signal line at the designs of the project, together with the associated fittings.. Calculation per m of finished work. | m1 | 9.18 | 0
3 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings .Calculation per m of finished work. | m1 | 36 | 0
4 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 54 | 0
5 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 3.2 | 0
6 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 14.4 | 0
7 | Supply and installation of water pipes ducktail Ø 4 "together with associated fittings. Calculation per m of finished work. | m1 | 26.88 | 0
| Supply of control valve for the wet signal system Ø 4“. | pcs | 2 | 0
8 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | pcs | 2 | 0
9 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | pcs | 2 | 0
10 | Supply of gate valve with oval body PN10 DN 80 | pcs | 2 | 0
11 | Supply and installation of non-return valve Ø 4 at the inlet line for sprinkler network.
|  | pcs | 2 | 0
12 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 2.3 | 0
13 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | pcs | 1 | 0
14 | Supply and installation of connectors for connection Ø 3" fire engines (double type connector).
|  | pcs | 1 | 0
15 | Supply and installation of flat leaky ball valve Φ 1 "in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property. | pcs | 2 | 0
16 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. really built on the property. | pcs | 2 | 0
17 | Supply and installation of sprinkler Φ1 "Calculation per 1 pc. really built on the property. | pcs | 96 | 0
18 | Supply and installation of ready pipe 13mm thick polyurethane insulation for pipes Φ 1 “together with all the necessary papers and materials. | m1
Calculation per m1 finished work.
19 | Supply and installation of ready pipe 13mm thick polyurethane insulation for pipes Φ 5/4 " along with all necessary papers and materials. | m1
Calculation per m1 finished work.
20 | Supply and installation of ready pipe 13mm thick polyurethane insulation for pipes Φ 2 " along with all necessary papers and materials. Calculation per m1 finished work. | m1
21 | Supply and installation of ready pipe 13mm thick polyurethane insulation for pipes Φ 3 " along with all necessary papers and materials. Calculation per m1 finished work. | m1
22 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 175.76 | 0
Calculation per m of finished work.
| TOTAL 2.3. ASSEMBLY WORK |  |  | 0
| TOTAL 2. SPRINKLER NETWORK |  |  | 0
3. SEWAGE
Sewage consists of drains with grates that are processed in
the architectural part of the project.
REKAPITULATION
1. PLUMBING |  |  |  | 0
2 SPRINKLER NETWORK |  |  |  | 0
TOTAL:
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit typeKNND d50 9/6-FM, FTT, RPDTA, KD, BD, L, VF***9/6 – A, FTT, RPDTA, L,VF (4100 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
- section of plate recuperator efficiency min. 60% in summer period
-Empty sections
-Section od steam humidifier with steam generator 20 kg/h
-Empty section
-Section of ventilator with direct drive, vertical --discharge, flow with two values 4100/ 2150 m3/h, external pressure drop 500 Pa
-Flexible connector
Air exhaust part:
- Flexible connector
- Suction section for vertical air intake
- Section of bag filter class F5
- Section of plate recuperator efficiency min. 60% in summer period
- Section of ventilators in anti explosive Ex performance with direct drive, vertical discharge, flow 4100/2150 m3/h, external pressure drop 500 Pa
- Blinds for waste air
- Flexible connector
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 30 kW at evaporating temperature and the outside temperature 50C to460C
- 25kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber, Cu pipes f 12,7/22 (met.20).
|  | pcs | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
| - electric motor drives of dampers with spring return | pcs | 1 | 0
4 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 950x550
-exhaust exterior steel grate
type AZR/ANŽ-4/3 size 950x550
- Diffuser model OD-11V/P/KR/I19/Ex/I19 in a panel 600x600 mm
| size 200 | pcs | 1 | 0
-Air flow regulator MRP-1/Ex iin front of OD 11/V
| size160 | pcs | 1 | 0
-wire damper for wall width L=200 mm
| PL-15 EL120S/A2/T12/Ex-Z | pcs
| Size 400x200 |  | 12 | 0
Size 500x350
| Pillar box made from stainless steel for removal of air from space type LN-3 from two strainers with filter F5 and manual flow regulation | pcs | 12 | 0
-height h= 2800, connector f 250
|  | pcs | 2 | 0
|  | pcs | 2 | 0
|  | pcs | 4 | 0
5 | Galvanized sheet metal ducts of square and circular diameter of plate 1.00 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 500 | 0
6 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
f 160
f 250
|  | m | 50 | 0
|  | m | 40 | 0
7 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 80 | 0
8 | Fine regulation, commissioning, testing capacity and quantity.
|  | commissioning | 1 | 0
Total air cinditioning equipment: |  |  |  | 0
| TOTAL OF MECH |  |  | 925785.8
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_13"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_13. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0 | 0
| TOTAL : |  |  | 0
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x50 mm2 (GRO -DO-TS) | m | 100 | 0 | 0
| NHXH E60 4x35mm2 | m | 30 | 0 | 0
| PPOO 4x16mm2 | m | 15 | 0 | 0
| PPOO-Y 5x10 mm2 | m | 13 | 0 | 0
| PPOO-Y 5x4 mm2 | m | 14 | 0 | 0
| PPOO-Y 5x2,5 mm2 | m | 5 | 0 | 0
| PPOO-Y 5x1,5 mm2 | m | 15 | 0 | 0
| PPOO-Y 3x2,5 mm2 | m | 5 | 0 | 0
| PPOO-Y 1x35 mm2 | m | 30 | 0 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 50 | 0 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 5 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0 | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0 | 0
| PNK 200 | m | 20 | 0 | 0
| PNK 300 | m | 25 | 0 | 0
| Slat cable carriers 200 mm | m | 20 | 0 | 0
| Slat cable carriers 300 mm | m | 25 | 0 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 15 | 0 | 0
3 | Other small material | flat | 1 | 0 | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 18 | 0 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 3 | 0 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 4 | 0 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 2 | 0 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 2 | 0 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 2 | 0 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0 | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 24 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 4 | 0 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 35 | 0 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 60 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0 | 0
| .serial water-proof n/ž | piece | 3 | 0 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0 | 0
| SKX 12/22 Serial switch SMS 03/8 - switch actuator SMO 17/5 - cable gland SPU 25, Type: SKX 12/22, TEP | piece | 1 | 0 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 2 | 0 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 2 | 0 | 0
11 | Other small material | flat | 1 | 0 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 20 | 0 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 5 | 0 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 50 | 0 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 3 | 0 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0 | 0
8. | Other small material | flat | 1 | 0 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 4 | 0 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 10 | 0 | 0
6 | Creating bypass Gauge | piece | 1 | 0 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0 | 0
8 | Testing of installed installations | pšl | 1 | 0 | 0
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 4 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 90 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 4 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 110 | 0 | 0
| -PP00-Y 3x2,5 mm2 | m. | 25 | 0 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 100 | 0 | 0
| - PVC warning tape | met | 100 | 0 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0 | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 4 | 0 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 4 | 0 | 0
3. | Protective canopy drip-channel for detector. | piece | 4 | 0 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 4 | 0 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 4 | 0 | 0
7. | Marking elements with persistent marks | piece | 4 | 0 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | 0
TOTAL FLAME DETECTORS : |  |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 3 | 0 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 2 | 0 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 2 | 0 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 4 | 0 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 17 | 0 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 16 | 0 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0 | 0
18. | Marking elements with persistent marks | piece | 10 | 0 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0 | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0 | 0
6. | Marking elements with persistant marks | piece | 2 | 0 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0 | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0 | 0
5. | Marking elements with persistant marks | piece | 1 | 0 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0 | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0 | 0
| Cabinet includes: | piece | 1 | 0 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0 | 0
4. | Marking elements with persistent marks | piece | 2 | 0 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 7 | 0 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 7 | 0 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 35 | 0 | 0
9. | Other unspecified fine material. | m. | 15 | 0 | 0
| SUB TOTAL |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
| . delivery of documentation (manual handling and programming, diary devices and certificates) |  |  |  | 0
. Handover and assembling the record on safety and functional testing.
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
| Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels): |  |  |  | 0
| SON 16-K | pieces | 80 | 0
Roof equipment:
| Wall cabinet for measurement: |  |  |  | 0
| ZON 05, Rf 20522 | pieces | 4 | 0
| Wall brackets (for the height difference): |  |  |  | 0
| ZON 03, Rf20322 | pieces | 2 | 0
Contact elements:
| Bonding wire-wire connectors: |  |  |  | 0
| KON 08; Rf 50111 | pieces | 8 | 0
| Tags for measuring site: |  |  |  | 0
| MŠ , Rf 80 122 | pieces | 4 | 0
| Measuring tape-wire connectors: |  |  |  | 0
| KON 02, Rf 40 122 | pieces | 4 | 0
| Drip: |  |  |  | 0
| KON 21; Rf 200212 | pieces | 4 | 0
| Impact point-Spitz: |  |  |  | 0
| LOV Rf 300400 | pieces | 3 | 0
| Interlocking Coupler (for horizontal gutters): |  |  |  | 0
| KON 06 Rf 60122 | pieces | 4 | 0
| Contact connectors (for grounding metal mass inside the building) |  |  |  | 0
| KON 05; Rf 80529 | pieces | 30 | 0
| Contact connectors (for switching cathing sticks to the strip grounding): |  |  |  | 0
| KON 07; Rf 40611 | pieces | 7 | 0
Catching bats:
| Catching bat H= 13 m (circumferential parapet-complete with struts): |  |  |  | 0
| LOP 13 ; Rf 300513 | pieces | 7 | 0
Lightning conductor:
| Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce): |  |  |  | 0
| RH 3 ; Rf 90150 | m | 80 | 0
Grounding:
| Strip grounding 30 x 3.5 mm (basic grounding + rampart): |  |  |  | 0
| RH 1; Rf 90701 | m | 200 | 0
| Crossing coupling tape-tape: |  |  |  | 0
| KON 01; Rf 50422 | kpl | 25 | 0
| Crossing coupling strip-Reinforcing steel (every 2 m): |  |  |  | 0
| KON 09; Rf 90122 | kpl | 45 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person) |  |  |  | 0
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor. |  |  |  | 0
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
| OUTDOOR LIGHTNING |  |  | 0
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
TOTAL OF ELE
TOTAL OF ELE+MECH

## B-14 MECH
3. BILL OF QUANTITY-HYDRO (B-14)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.8 | 0
Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x2. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS |  |  |  | 0
1.2. CONCRETE WORKS
1 | Making the connecting shafts of concrete, MB 20 in the corresponding panel. The size and shape of the detail. To carry out treatment on walls and install creepers. | m3 | 1.1 | 0
1,2x1,2x0,35x1 + 0,8x0,75x1 =
1.2. TOTAL CONCRETE WORKS |  |  |  | 0
1.3. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
3 | Supply and installation of cover 80x80 and transport capacity 25 tones | kom | 1 | 0
TOTAL 1.3. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
1.4. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 24.45 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 8.88 | 0
Calculation per m of finished work
3 | Supply and installation of galvanized steel plumbing Φ ¾“ (DN20mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 5.24 | 0
4 | Supply and installation of galvanized steel plumbing Φ ½“ (DN15mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 3.87 | 0
5 | Supply and installation of flat leaky ball valve Φ 1" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 4 | 0
| Calculation per 1 pc. really built on the property. |  |  | 0
6 | Supply and installation of flat leaky ball valve Φ ½“ on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | Psc. | 2 | 0
Calculation per 1 pc. really built on the property.
7 | Supply and installation of ball valves with lever and unions Φ 1 " | psc. | 47 | 0
Calculation per 1 pc. really built on the property.
8 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 177.69 | 0
Calculation per m1 finished work.
TOTAL 1.4. ASSEMBLY WORK |  |  |  | 0
1.5 | SANITARY APPLIANCES AND SANITARY WARE
SANITARY APPLIANCES AND ACCESSORIES
Note:
The contractor should offer type and color of the sanitary equipment in agreement with an investor or an architect, and then approach contracting and total access and installation of the same order. Sanitary ware and fittings must be first-class (white), with chrome and feeders, like the type GEBERIT, GROHE, DOLOMITE, LAUFEN or equivalent. Ports-microclimate of supply and sanitary sewers run after approval by investors.
1 | Toilet bowl
Supply and installation of toilet bowls made of first class faience (sanitary ware), white color, and fully functional version with full plastic toilet cover and seat, toilet tank (low mounting) with angle valve and drain in the floor. Calculation per piece of fully installed toilet bowl.
|  | Psc | 1 | 0
2 | Sink
Supply, transmission and assembly of first class faience sink, approx. 55 cm, together with chrome drainage tube and connecting material, one-hand mixer for hot and cold water, and angle valve Ø 1/2 "and all connecting material.
Calculation per piece of fully built sink.
|  | Psc | 1 | 0
3 | Sanitary accessories
Supply and installation of sanitary ware (class I - INOX, or Kimberly-Clark or equivalent) with:
| a) toilet cleaning kit | Psc | 1 | 0
| b) toilet paper holder | Psc | 1 | 0
| c) wall mirror, dimensions 600 x 400 mm, thickness 4 mm, with polished edges | psc | 1 | 0
| d) paper towel holder | Psc
| e) bowl for liquid soap | Psc | 1 | 0
TOTAL 1.5 SANITARY APPLIANCES AND SANITARY WARE |  |  |  | 0
TOTAL 1. PLUMBING |  |  |  | 0
2. SEWAGE
1.1. EARTHWORKS
1 | Manual excavation of a trench width 80cm in materials of categories III and IV , along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.8 | 0
Calculation per m3 of finished work.
(2x0, 90x0, 6 x12.x12 +1.2) =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3 of finished work.
(2x0, 60x0, 2) =
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1 | 3.08 | 0
Calculation per m3 of finished work.
(2.81 to 0.24) x 1.2) =
TOTAL 2.1. EARTHWORKS |  |  |  | 0
2.2. CONCRETE WORKS
1 | Making the connecting shafts of concrete, MB 20 in the corresponding panel. The size and shape of the detail. To carry out treatment on walls and install creepers. | m3 | 1.1 | 0
1,2x1,2x0,35x1 + 0,8x0,75x1 =
TOTAL 2.2 CONCRETE WORKS |  |  |  | 0
2.3. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
3 | Providing drainage pipes to a height of 360 cm from the upper level of the flat roof. | psc | 1 | 0
size 25x25 cm
4 | Supply and installation of cover with transport capacity of 25 tones and with dimensions 80x80 | psc | 1 | 0
TOTAL 2.3. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
2.4 | ASSEMBLY WORK
Procurement of materials, transportation, installation, thermal insulation, functional and pressure test.
1 | PVC sewer pipes for home sewers.
Supply and installation of PVC sewer pipes for the performance of internal sewage system, according to DIN 8061 and DIN 19531, with all necessary wiring and fittings and small installation material. Perform sealing sewer pipes with rubber rings. Bid to define the exact type of offered sewer, pipes with a certificate that guarantees the quality of pipes and fittings attached. Mandatory sample and approval before making the installation and approved by supervision, by the enrollment in the construction diary. Pipes of dubious quality, without adequate documentation, are forbidden to install. Mandatory photo documentation of built status before backfilling the trench in paragraph 1.1.).
This item includes all the work and all materials, pipe fittings, auxiliary material for joining and fixing - clips for fixed and sliding points.
Calculation per m of built sewers.
| DN 110 | m | 11.87 | 0
| DN 50 | m | 1.37 | 0
2 | PVC sewer revision / sweepers
Supply and installation of PVC sewer audit / sweepers for installation in the bottom of the control shaft AB.
Calculation per piece embedded audit / sweepers.
DN 110
psc
|  |  | 1 | 0
3 | TOP drainage tube
Procurement, supply and installation of the plastic top siphon with horizontal drains diameter Ø50 mm with a grid of stainless steel measuring 150 x 150 mm.
Calculation per piece integrated top siphon.
|  | psc | 1 | 0
4 | PVC ventilation cap
Supply and installation of vertical sewer vent caps, along with copper flashings including a link to waterproof (as type Braas or equivalent). Ventilation cap (set) Ø 50 mm.
Calculation per piece fitted caps.
|  | Psc | 1 | 0
5 | Testing the building sewage
Testing of complete sewage facility with associated buildings pane and header tanks, etc. on the bandwidth and functionality. Testing performed prior to closing pipeline trenches and painting with photographic documentation of the required item 1.1. After successful completion of testing the functionality and impermeability, issue a certificate about the same. Development of rules / instructions on the operation and maintenance of the entire drainage system of the building is included in this item.
Calculation per m of tested network.
|  | m | 13.42 | 0
TOTAL 2.4. ASSEMBLY WORK |  |  |  | 0
TOTAL 2. SEWAGE |  |  |  | 0
3. SPRINKLER NETWORK
3.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 3,1. EARTHWORKS |  |  |  | 0
3.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 2 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
| Calculation per piece. |  |  | 0
TOTAL 3.2. MASONRY AND BRICKLAYERING WORK
3.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for emptying of sprinkler network, together with the associated fittings. Calculation per m of finished work | m1 | 8.85 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for drain line near signal valve according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 14.13 | 0
3 | Supply and installation of steel galvanized water pipes Φ 1 "(DN25mm), with the connections, for cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 34.72 | 0
4 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN32mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 19.84 | 0
5 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN40mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 4.96 | 0
6 | Supply and installation of galvanized steel plumbing Φ 2 "(DN50mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 4.4 | 0
7 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 36.79 | 0
8 | Supply and installation of water pipes ducktail Ø 4"together with associated fittings. Calculation per m of finished work. | m1 | 9.6 | 0
9 | Supply and installation of DUCTIL water pipes Ø 8“ together with associated | m1 | 12 | 0
10 | Supply control valve for the dry signal system on Ø 4“. | psc | 4 | 0
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 4 | 0
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 4 | 0
13 | Supply of gate valve with oval body PN10 DN 100 | psc | 4 | 0
14 | Supply of gate valve with oval body PN10 DN 200 | psc | 1 | 0
15 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network. |  |  | 0
0
|  | psc | 1 | 0
16 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 4.16 | 0
17 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks. |  |  | 0
0
|  | psc | 1 | 0
18 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector). |  |  | 0
0
|  | psc | 1 | 0
19 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc. | 4 | 0
20 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. Really built on the property. | psc. | 4 | 0
21 | Supply and installation of sprinkler Φ1" with capacity of 0,56 l/s Calculation per 1 pc. Really built on the property. | psc | 64 | 0
22 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 149.15 | 0
Calculation per m of finished work.
TOTAL 3.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 3. SPRINKLER NETWORK |  |  |  | 0
4. PRECIPITATOR
4.1. | EARTHWORKS
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 31.24 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 18.72 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 15.02 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 2.68 | 0
TOTAL EARTHWORKS |  |  |  | 0
4.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 1.08 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 3.86 | 0
3 | Fabrication and installation of armor for the bottom plate and walls. |  | 31.24 | 0
| MC 30 | Kg
| RA 400/500 | Kg
| TOTAL CONCRETE WORKS |  |  | 0
4.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 6 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | Psc | 2 | 0
| Dim. 80x90 cm | Psc | 2 | 0
| Dim. 80x95 | Psc | 2 | 0
4.3 | TOTAL ASSEMBLY WORK |  |  | 0
4 | TOTAL PRECIPITATOR |  |  | 0
RECAPITULATION
| 1. PLUMBING |  |  | 0
| 2.SPRINKLER NETWORK |  |  | 0
| 3.SEWAGE |  |  | 0
| 4. PRECIPITATOR |  |  | 0
| Total: |  |  | 0
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling type KNNL d50 9/9-FM, FTT, RPDTA, KDTA, L, VF***9/9-A, FTT, RPDTA, L, VF (5680 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
- Section of plate recuperator with efficiency min 60% in summer period
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 5860 m3/h, the external pressure drop 500 Pa
-Flexible connection
Drain part:
-Flexible connection
Suction-section of vertical air intake
Section-filtration fabric filter class F5
- section of plate recuperator efficiency min. 60% in summer period
-Section of ventilator with direct drive, vertical discharge in »Ex« execution, flow with two values 5860 m3/h, external pressure drop 500 Pa
-Flexible connector
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 40,8 kW at evaporating temperature 5° and the outside temperature 460C
- 20 kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
set
|  |  | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
-elements of automation within the air chambers in the explosion-proof design
|  | set | 1 | 0
4 | -Equipment of the system for humidifying air. In all of the EMA as Hr.
-Pump Station high pressure
Condair HP100 with VFD capacity of water
5 ÷ 200 kg / h, N = 0.5 kW
| -Droplet eliminator Condair HP | Pcs | 1 | 0
size 600x300
| -System from the line with seven nozzles Condor HP capacity is 4.5 l / h | Pcs | 3 | 0
-Condor 3 HP, valve block of 3 valves with seven degrees of ventilation
| -HST 010 duct humidity sensor | Pcs | 3 | 0
-Condor HP Slave
| -Pipeline from f1/4'' | Pcs | 3 | 0
| Complete with commissioning | Pcs | 3 | 0
|  | Pcs | 2 | 0
|  | Pcs | 30 | 0
5 | Equipment for air distribution like of the Hidra Sl.in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 950x850
- exhaust exterior steel grate
Type AZR/ANŽ-4/3 size 950x850
- Diffuser for air supply with a box, model OD-11V/S/I19/Ex in plate 600x600mm
| size 315 | Pcs | 1 | 0
-air flow regulator MRP-1/Ex in front of OD-11/V
| Size 250 | Pcs | 1 | 0
- volume control damper RŽ-2/Ex-Z
| size 600x350 | Pcs
| - fire-damper wall width = 400 |  | 6 | 0
| PL-15 EL120S/A2/T12/Ex-Z | Pcs
| Size 600X350 |  | 3 | 0
| Size 500x350 | Pcs
| Size 300X350 |  | 3 | 0
- Mounted box for the removal of air from the space type LN-3 from two strainer with filter F5 and manual control flow made ​​of stainless steel
height h = 2800, port f 250
|  | Pcs | 4 | 0
|  | Pcs | 4 | 0
|  | Pcs | 4 | 0
|  | Pcs | 5 | 0
6 | Galvanized sheet metal ducts 1,00 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 950 | 0
7 | Aluminum flexible pipes with insulation of mineral wool 25mm and outer sheath made from aluminum foil f 250
|  | m | 10 | 0
8 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 150 | 0
9 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
Total air conditioning equipment: |  |  |  | 0
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m | pcs
|  |  | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 40 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 14 | 0
5 | Delivery and installation of galvanized steel pipe T pieces- T piece 1/2"
|  | pcs | 6 | 0
6 | Supply and installation of valves for compressed air with connection for flexible hose.
- R 1/2"
|  | pcs | 5 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 4 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 14 | 0
9 | Small materials for bonding, rosette for pipes, etc. | all inclusive | 1 | 0
10 | Production of construction pipe penetrations 1/2 "through the wall (5 pcs.) finished with | All inclusive
|  |  | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | All inclusive
|  |  | 1 | 0
Total equipment for compressed air: |  |  |  | 0
| TOTAL OF MECH |  |  | 747021.83
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_14"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_14. (See related scheme 1.4.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.K_14. (See related scheme 1.5.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
| TOTAL : |  |  | 0
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x70 mm2 (GRO -DO-TS) | m | 50 | 0
| NHXH E60 4x35mm2 | m | 25 | 0
| PPOO 4x16mm2 | m | 20 | 0
| PPOO-Y 5x6 mm2 | m | 15 | 0
| PPOO-Y 5x2,5 mm2 | m | 10 | 0
| PPOO-Y 5x1,5 mm2 | m | 25 | 0
| PPOO-Y 3x2,5 mm2 | m | 25 | 0
| PPOO-Y 1x25 mm2 | m | 25 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 90 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 20 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0
| PNK 200 | m | 30 | 0
| Slat cable carriers 200 mm | m | 30 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 25 | 0
3 | Other small material | flat | 1 | 0
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 16 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 9 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 1 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 5 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 10 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 2 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 36 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 7 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 30 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 45 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0
| .serial water-proof n/ž | piece | 1 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 6 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 3 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 45 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 50 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 3 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 30 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 2 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 4 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 2 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 5 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 5 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 6 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 110 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 10 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm | m | 120 | 0
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 4 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 120 | 0
| -PP00-Y 3x2,5 mm2 | m. | 25 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 30 | 0
| - PVC warning tape | met | 30 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 4 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 4 | 0
3. | Protective canopy drip-channel for detector. | piece | 4 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 3 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 3 | 0
7. | Marking elements with persistent marks | piece | 3 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
| TOTAL FLAME DETECTORS : |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 7 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 4 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 2 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 3 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 3 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 15 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 6 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 6 | 0
18. | Marking elements with persistent marks | piece | 6 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 3 | 0
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0
6. | Marking elements with persistant marks | piece | 2 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 1 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 4 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0
9. | Other unspecified fine material. | m. | 15 | 0
| SUB TOTAL |  |  | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 150 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 6 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 16 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 6 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 6 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 6 | 0
Drip:
| KON 21; Rf 200212 | pieces | 10 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 6 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 10 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 12 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 6 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 6 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 170 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 290 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 20 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 80 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
| OUTDOOR LIGHTNING |  |  | 0
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
TOTAL OF ELE
TOTAL OF ELE+MECH

## B-16 MECH
3. BILL OF QUANTITY-HYDRO (B-16)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work. 2x0,90x0,6+1.2x12.x12. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work. 2x0,60x0,2
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. (2,81-0,24) x 1,2
| TOTAL 1.1. EARTHWORKS |  |  | 0
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of RC structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 1.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 26.16 | 0
Calculation per m of finished work
2 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | pcs | 3 | 0
Calculation per 1 pc. really built on the property.
3 | Supply and installation of ball valves with lever and unions Φ 1 " | pcs | 2 | 0
Calculation per 1 pc. really built on the property.
4 | Testing od installation by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 26.16 | 0
Calculation per m1 finished work.
TOTAL 1.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 1. PLUMBING |  |  |  | 0
2. SPRINKLER NETWORK
2.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV , along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
| TOTAL 2.1. EARTHWORKS |  |  | 0
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of RC structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
| TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  | 0
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 7.79 | 0
2 | Supply and installation of galvanized steel plumbing Φ 1" (DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings .Calculation per m of finished work. | m1 | 19.6 | 0
2 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings .Calculation per m of finished work. | m1 | 13 | 0
3 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings .Calculation per m of finished work. | m1 | 6.5 | 0
4 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings .Calculation per m of finished work. | m1 | 1.34 | 0
5 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings .Calculation per m of finished work. | m1 | 14.07 | 0
6 | Supply and installation of water pipes ducktail Ø 4 "together with associated fittings. Calculation per m of finished work. | m1 | 12 | 0
7 | Supply of control valve for the wet signal system Ø 4“. | pcs | 1 | 0
8 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | pcs | 1 | 0
9 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | pcs | 1 | 0
10 | Supply of gate valve with oval body PN10 DN 80 | pcs | 2 | 0
11 | Supply and installation of non-return valve Ø 4 at the inlet line for sprinkler network. |  |  | 0
0
|  | pcs | 1 | 0
12 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 2.54 | 0
13 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | pcs | 1 | 0
14 | Supply and installation of connectors for connection Ø 3" fire engines (double type connector).
|  | pcs | 1 | 0
15 | Supply and installation of flat leaky ball valve Φ 1 "in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property. | pcs | 1 | 0
16 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. really built on the property. | pcs | 1 | 0
17 | Supply and installation of sprinkler Φ1 „capacity 0,7293 l/s. | pcs | 40 | 0
| Calculation per 1 pc. really built on the property. |  |  | 0
18 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 73.74 | 0
Calculation per m of finished work.
TOTAL 2.3. ASSEMBLY WORK |  |  |  | 0
TOTAL 2. SPRINKLER NETWORK |  |  |  | 0
3. SEWAGE
3.1. | EARTHWORKS
1 | Mechanical excavation of earth category III at depth of 0.3-5 m with tossing the earth at a distance of 1, 0 m from the edge of the excavation. | m3 | 15.62 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 9.36 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 7.51 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, backfilling and compacting gravel to the base of bottom plate of the septic, at a thickness of 20 cm | m3 | 1.34 | 0
TOTAL 3.1 EARTHWORKS |  |  |  | 0
3.2 | MASONRY AND BRICKLAYERING WORK
1 | Making the bottom plate of the septic from reinforced concrete MB 30 | m3 | 0.54 | 0
2 | Making the walls of reinforced concrete MB 30. Wall thickness d = 15 cm. Making the double-sided plate. | m3 | 1.93 | 0
3 | Fabrication and installation armature
for the lower plate and the walls.
| MC 30 | kg
| RA 400/500 | kg
TOTAL MASONRY AND BRICKLAYERING WORK
3.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings of diameter 200 | pcs | 3 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | pcs | 1 | 0
| Dim. 80x90 cm | pcs | 1 | 0
| Dim. 80x95 | pcs | 1 | 0
TOTAL ASSEMBLY WORK |  |  |  | 0
3 | TOTAL SEWAGE |  |  | 0
REKAPITULATION
1. PLUMBING |  |  |  | 0
2 SPRINKLER NETWORK |  |  |  | 0
3 SEWAGE |  |  |  | 0
TOTAL: |  |  |  | 0
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit like types: KNNL d50 6/6-FM, FTT, KDTA, L, VF (2300 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 160C /59% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 7100 m3 / h, the external pressure drop 500 Pa
-Flexible connection
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 32 kW at evaporating temperature and the outside temperature 50C to 460C
- 20kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
|  | set | 1 | 0
4 | Roof radial fan in the anti-explosive performance as the Clima Celje, Slovenia.
Type EX SVK2-450/400-4/6,N=1,0/0,35 kW.
Some of the equipment cooling fan are:
- Flexible connector
- Auto -lift shutters
- Flange
- Supporting structure for the pitched roof in thermal protection
- Frequency regulator for speed control
|  | set | 1 | 0
5 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
Type APZR/ANŽ-4/3 size 650x550
- Diffuser for air supply with a box, model
OD-11V/S/I19/Ex u ploči 600x600 mm
Size 200
| Size 250 | pcs | 1 | 0
-air flow regulator MRP-1/Ex in front of OD-11/V
Size 160
| Size 200 | pcs | 6 | 0
| -fire damper for wall, width L= 200 | pcs | 2 | 0
PL-15 EL120S/A2/T12/Ex-Z
| Size 300x300 | pcs | 6 | 0
| Size 300x250 | pcs | 2 | 0
Size 500x250
Pillar box for air removal from space type LN-3 from two strainer with filter, class F5 and manual flow regulation made from inox
| -height h= 3400, connector f 250 | pcs | 1 | 0
|  | pcs | 1 | 0
|  | pcs | 1 | 0
|  | pcs | 3 | 0
6 | Galvanized sheet metal ducts of square and circular diameter of plate 0.8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 440 | 0
7 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
f 160
f 250
|  | m | 25 | 0
|  | m | 10 | 0
8 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 70 | 0
9 | Fine regulation, commissioning, testing capacity and quantity.
|  | commissioning | 1 | 0
Total air conditioning equipment: |  |  |  | 0
No | An item of bill of quantities –heat substation- delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Heat substation
Fin heat exchanger of 100 kW
- Primary side water 130/900C, dp = 2000P
- Secondary side water 90/700C, dp = 1500pa
Armour of substation
Valve with unions NP16
- R-1'', kom.4
- R 5/4'',kom.2
-Fill & drain R ½'' kom.2
Control circuit hot water
-regulating circuit,
- Electric line valve R 1'',
- Limit thermostat 900C,
- Initial temperature sensor,
- Spatial sensor
- Circulation pump Wilo
Star RS 30/8, N = 0.157 kW
- Expansion vessel shut V = 15 lit with sig. valve R3/4'',
- Pressure gauge 0-6 bar,
- Pressure gauge 0-16 bar,
- Thermometer 0-1200C AM,
- Thermometer 0-1800C,
- Connecting pipeline
| set | set | 1 | 0
Note: the primary pipeline is not subject of bill of quantities (provided by the investor)
Total heat substation: |  |  |  | 0
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m
|  | pcs | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 36 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 8 | 0
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 5 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 5 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 4 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 15 | 0
9 | Small materials for bonding, rozetne of pipes, etc. | all inclusive | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
Total equipment for compressed air: |  |  |  | 0
| TOTAL OF MECH |  |  | 355468.74
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_16"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_16. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0 | #REF!
| TOTAL : |  |  | 0
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x35 mm2 (GRO -DO-TS) | m | 100 | 0 | #REF!
| NHXH E60 4x25mm2 | m | 25 | 0 | #REF!
| PPOO 4x16mm2 | m | 15 | 0 | #REF!
| PPOO-Y 5x10 mm2 | m | 13 | 0 | #REF!
| PPOO-Y 5x2,5 mm2 | m | 12 | 0 | #REF!
| PPOO-Y 5x1,5 mm2 | m | 10 | 0 | #REF!
| PPOO-Y 3x2,5 mm2 | m | 5 | 0 | #REF!
| PPOO-Y 1x25 mm2 | m | 25 | 0 | #REF!
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 20 | 0 | #REF!
3 | Sealing cables crossing between fire fireproof sector mass | kg | 5 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0 | #REF!
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0 | #REF!
| TOTAL II : |  |  | 0
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0 | #REF!
| PNK 200 | m | 20 | 0 | #REF!
| Slat cable carriers 200 mm | m | 20 | 0 | #REF!
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 10 | 0 | #REF!
3 | Other small material | flat | 1 | 0 | #REF!
| TOTAL III: |  |  | 0
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 8 | 0 | #REF!
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 2 | 0 | #REF!
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 12 | 0 | #REF!
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 2 | 0 | #REF!
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 1 | 0 | #REF!
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 1 | 0 | #REF!
7. | Other unspecified material needed for the installation | kpl | 1 | 0 | #REF!
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0 | #REF!
| TOTAL IV : |  |  | 0
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 10 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 3 | 0 | #REF!
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 20 | 0 | #REF!
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 25 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0 | #REF!
| .serial water-proof n/ž | piece | 1 | 0 | #REF!
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 2 | 0 | #REF!
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0 | #REF!
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0 | #REF!
11 | Other small material | flat | 1 | 0 | #REF!
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | #REF!
| TOTAL V.1 : |  |  | 0
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 14 | 0 | #REF!
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 5 | 0 | #REF!
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0 | #REF!
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 40 | 0 | #REF!
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0 | #REF!
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 3 | 0 | #REF!
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0 | #REF!
8. | Other small material | flat | 1 | 0 | #REF!
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | #REF!
| TOTAL VI: |  |  | 0
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0 | #REF!
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 4 | 0 | #REF!
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0 | #REF!
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0 | #REF!
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 8 | 0 | #REF!
6 | Creating bypass Gauge | piece | 1 | 0 | #REF!
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0 | #REF!
8 | Testing of installed installations | pšl | 1 | 0 | #REF!
| TOTAL VII: |  |  | 0
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 3 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 70 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 1 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 30 | 0 | #REF!
| -PP00-Y 3x2,5 mm2 | m. | 6 | 0 | #REF!
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 30 | 0 | #REF!
| - PVC warning tape | met | 30 | 0 | #REF!
9 | Other small material for mounting and connecting | flat | 1 | 0 | #REF!
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0 | #REF!
Note: Quote does not cover construction work on the excavation and backfilling the trench!
| TOTAL VIII KM: |  |  | 0
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0 | #REF!
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0 | #REF!
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0 | #REF!
| TOTAL IX: |  |  | 0
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 2 | 0 | #REF!
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 2 | 0 | #REF!
3. | Protective canopy drip-channel for detector. | piece | 2 | 0 | #REF!
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0 | #REF!
5. | Cable glands for Exd enclosure M25x15mm. | piece | 2 | 0 | #REF!
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 2 | 0 | #REF!
7. | Marking elements with persistent marks | piece | 2 | 0 | #REF!
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | #REF!
| TOTAL FLAME DETECTORS : |  |  | 0
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 3 | 0 | #REF!
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0 | #REF!
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 2 | 0 | #REF!
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0 | #REF!
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0 | #REF!
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0 | #REF!
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0 | #REF!
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0 | #REF!
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0 | #REF!
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 11 | 0 | #REF!
11. | Supply and delivery of mark elements for the fire alarm system | piece | 7 | 0 | #REF!
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0 | #REF!
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0 | #REF!
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0 | #REF!
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0 | #REF!
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0 | #REF!
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0 | #REF!
18. | Marking elements with persistent marks | piece | 7 | 0 | #REF!
19. | Other unspecified fine material. | kpl. | 1 | 0 | #REF!
20. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0 | #REF!
| TOTAL MANUAL TRANSMITTER |  |  | 0
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | #REF!
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0 | #REF!
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0 | #REF!
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0 | #REF!
6. | Marking elements with persistant marks | piece | 2 | 0 | #REF!
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0 | #REF!
| TOTAL SIRENS : |  |  | 0
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0 | #REF!
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0 | #REF!
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0 | #REF!
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0 | #REF!
5. | Marking elements with persistant marks | piece | 1 | 0 | #REF!
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0 | #REF!
| TOTAL FLASHES: |  |  | 0
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0 | #REF!
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0 | #REF!
| Cabinet includes: | piece | 1 | 0 | #REF!
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0 | #REF!
4. | Marking elements with persistent marks | piece | 2 | 0 | #REF!
5. | Other unspecified fine material. | kpl. | 1 | 0 | #REF!
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0 | #REF!
7. | ATTESTS FOR EX EQUIPMENT
| Creating attests authorized by the domestic industry. |  |  | 0
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0 | #REF!
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 4 | 0 | #REF!
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0 | #REF!
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0 | #REF!
5. | Other unspecified fine material. | kpl. | 1 | 0 | #REF!
6. | Installation and connection of equipment | kpl. | 1 | 0 | #REF!
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0 | #REF!
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0 | #REF!
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0 | #REF!
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 15 | 0 | #REF!
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 15 | 0 | #REF!
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0 | #REF!
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0 | #REF!
9. | Other unspecified fine material. | m. | 15 | 0 | #REF!
| SUB TOTAL |  |  | 0
9.8. | COMMISSIONING (START UP) |  |  |  | #REF!
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
| TOTAL COMMISSIONING : |  |  | 0
| TOTAL IX |  |  | 0
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
| Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels): |  |  |  | #REF!
| SON 16-K | pieces | 50 | 0
Roof equipment:
| Wall cabinet for measurement: |  |  |  | #REF!
| ZON 05, Rf 20522 | pieces | 4 | 0
| Wall brackets (for the height difference): |  |  |  | #REF!
| ZON 03, Rf20322 | pieces | 4 | 0
Contact elements:
| Bonding wire-wire connectors: |  |  |  | #REF!
| KON 08; Rf 50111 | pieces | 6 | 0
| Tags for measuring site: |  |  |  | #REF!
| MŠ , Rf 80 122 | pieces | 4 | 0
| Measuring tape-wire connectors: |  |  |  | #REF!
| KON 02, Rf 40 122 | pieces | 4 | 0
| Drip: |  |  |  | #REF!
| KON 21; Rf 200212 | pieces | 12 | 0
| Impact point-Spitz: |  |  |  | #REF!
| LOV Rf 300400 | pieces | 6 | 0
| Interlocking Coupler (for horizontal gutters): |  |  |  | #REF!
| KON 06 Rf 60122 | pieces | 12 | 0
| Contact connectors (for grounding metal mass inside the building) |  |  |  | #REF!
| KON 05; Rf 80529 | pieces | 20 | 0
| Contact connectors (for switching cathing sticks to the strip grounding): |  |  |  | #REF!
| KON 07; Rf 40611 | pieces | 4 | 0
Lightning conductor:
| Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce): |  |  |  | #REF!
| RH 3 ; Rf 90150 | m | 45 | 0
Grounding:
| Strip grounding 30 x 3.5 mm (basic grounding + rampart): |  |  |  | #REF!
| RH 1; Rf 90701 | m | 70 | 0
| Crossing coupling tape-tape: |  |  |  | #REF!
| KON 01; Rf 50422 | kpl | 16 | 0
| Crossing coupling strip-Reinforcing steel (every 2 m): |  |  |  | #REF!
| KON 09; Rf 90122 | kpl | 40 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
| TOTAL X : |  |  | 0
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person) |  |  |  | #REF!
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor. |  |  |  | #REF!
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS |  |  | 0
II) | POWER CABLES |  |  | 0
III) | CABLE CARRIERS AND INSTALLATION PIPES |  |  | 0
IV) | FLASHLIGHTS |  |  | 0
V) | ILIGHTNING INSTALLATION |  |  | 0
VI) | OUTLET AND FEEDER INSTALLATIONS |  |  | 0
VII) | POTENTIAL EQUALIZING INSTALLATIONS |  |  | 0
| OUTDOOR LIGHTNING |  |  | 0
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE |  |  | 0
IX) | FIRE DETECTION SYSTEM |  |  | 0
X) | LIGHTNING ROD INSTALLATION |  |  | 0
XI) | TESTING AND MESAURING |  |  | 0
XII) | PROJECT OF CREATED STATE |  |  | 0
| TOTAL OF ELE |  |  | 0
TOTAL OF ELE+MECH

## B-17 MECH
3. BILL OF QUANTITY-HYDRO (B-17)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x1.
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
| TOTAL 1.1. EARTHWORKS |  |  | 0
1.2 CONCRETE WORKS
1 | Making the connecting shafts of concrete, MB 20 in the corresponding panel. The size and shape of the detail. To carry out treatment on walls and install of creepers. | m3 | 1.1 | 0
1,2x1,2x0,35x1 + 0,8x0,75x1 =
TOTAL 1.2 CONCRETE WORK |  |  |  | 0
1.3. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
3 | Supply and installation of the cover size 80x80 and transport capcacity of 25 tones. Calculation per pieces | psc | 1 | 0
TOTAL 1.3. MASONRY AND BRICKLAYERING WORK
1.4. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 26.93 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 24.71 | 0
Calculation per m of finished work
3 | Supply and installation of flat leaky ball valve Φ 2" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 1 | 0
Calculation per 1 pc. really built on the property.
4 | Supply and installation of flat leaky ball valve Φ 1" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 5 | 0
Calculation per 1 pc. really built on the property.
5 | Supply and installation of ball valves with lever and unions Φ 1 " | psc. | 5 | 0
Calculation per 1 pc. really built on the property.
8 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 51.67 | 0
Calculation per m1 finished work.
TOTAL 1.4. ASSEMBLY WORK
TOTAL 1. PLUMBING
2. SPRINKLER NETWORK
2.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 2,1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 2 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for drain line near signal valve, together with the associated fittings according to the plans of the project. Calculation per m of finished work | m1 | 11.49 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for emptying of sprinkler network, together with the associated fittings. Calculation per m of finished work | m1 | 4.6 | 0
3 | Supply and installation of steel galvanized water pipes Φ 1 "(DN25mm), with the connections, for cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 9.2 | 0
4 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN32mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 4.6 | 0
5 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN40mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 0 | 0
6 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 1 | 0
7 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 2 | 0
8 | Supply and installation of water pipes ducktail Ø 4"together with associated fittings. Calculation per m of finished work. | m1 | 25 | 0
9 | Supply and installation of DUCTIL water pipes Ø 8“ together with associated | m1 | 14 | 0
10 | Supply control valve for the dry signal system on Ø 3“. | psc | 3 | 0
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 3 | 0
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 3 | 0
13 | Supply of gate valve with oval body PN10 DN 80 | psc | 3 | 0
14 | Supply of gate valve with oval body PN10 DN 20 | psc | 3 | 0
15 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network. |  | 1 | 0
psc
16 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 2.11 | 0
17 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | psc | 1 | 0
18 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector).
|  | psc | 1 | 0
19 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc. | 5 | 0
20 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 72.09 | 0
Calculation per m of finished work.
TOTAL 2.3. ASSEMBLY WORK
TOTAL 2. SPRINKLER NETWORK
3. PRECIPITATOR
3.1. | EARTHWORKS
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 31.24 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 18.72 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 15.02 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 2.68 | 0
TOTAL EARTHWORKS
3.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 1.08 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 3.86 | 0
3 | Fabrication and installation of armor for the bottom plate and walls. |  | 31.24 | 0
| MC 30 | Kg
| RA 400/500 | Kg
TOTAL CONCRETE WORKS
3.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 6 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | Psc | 2 | 0
| Dim. 80x90 cm | Psc | 2 | 0
| Dim. 80x95 | Psc | 2 | 0
3.3 | TOTAL ASSEMBLY WORK
3 | TOTAL PRECIPITATOR
RECAPITULATION
1. PLUMBING
2.SPRINKLER NETWORK
3. PRECIPITATOR
Total:
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit type KNND d50 12/9-FM, FTT, RPDTA, KD,BD, L, VF***12/9-A, FTT, RPDTA, L, VF, (7200 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
- section of plate recuperator efficiency min. 60% in summer period
-Empty sections
-Section of ventilator with direct drive, vertical discharge, flow with two values 7200/ 2150 m3/h, external pressure drop 500 Pa
-Flexible connector
Air exhaust part:
- Flexible connector
- Suction section for vertical air intake
- Section of bag filter class F5
- Section of plate recuperator efficiency min. 60% in summer period
- Section of ventilators in anti explosive Ex performance with direct drive, vertical discharge, flow 7200/2150 m3/h, external pressure drop 500 Pa
- Blinds for waste air
- Flexible connector
Set
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 45 kW at evaporating temperature and the outside temperature 50C to 460C
- 30kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
|  | set | 1 | 0
4 | Roof radial fan in the anti-explosive performance as the Clima Celje, Slovenia.
type EX SVK2-500/450-4/6,N=1,3/0,90 kW.
Some of the equipment cooling fan are:
- Flexible connector
- Auto -lift shutters
- Flange
- Supporting structure for the pitched roof in thermal protection
- Frequency regulator for speed control
|  | set | 2 | 0
5 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 1250x850
- exhaust exterior steel grate
Type AZR/ANŽ-4/3 size 1250x850
- Diffuser for air supply with a box, model OD-11V/S/I19/Ex
| size 250 | pcs | 1 | 0
size315
| -air flow regulator MRP-1/Ex in front of OD-11/V | pcs | 1 | 0
Size 200
Size 250
| -fire damper for all width L= 500 | pcs | 8 | 0
| PL-15 EL120S/A2/T12/Ex-Z | pcs | 8 | 0
Size 800x400
| Size 600x400 | pcs | 8 | 0
| Size 300x300 | pcs | 8 | 0
Pillar box made from stainless steel for air removal from space type LN-3 from two strainers with filter F5 and manual flow regulation
-height h= 3600,connector f 250
| -suction grid size 800x600 in a box from galvanized sheet 1,0 mm, size 800x600x500 with connector f 400 | pcs | 4 | 0
|  | pcs. | 2 | 0
|  | pcs | 2 | 0
|  | pcs | 7 | 0
|  | pcs. | 2 | 0
6 | Galvanized sheet metal ducts of square and circular diameter of plate 1.00 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 1100 | 0
7 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
f 200
f 250
|  | m | 20 | 0
|  | m | 20 | 0
8 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 180 | 0
9 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
Total air cinditioning equipment:
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m | pcs
|  |  | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 52 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 14 | 0
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 6 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 5 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 4 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 15 | 0
9 | Small materials for bonding, rosette of pipes, etc. | all inclusive | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
Total equipment for compressed air:
No | An item of bill of quantities – thermal substation and thermal connection - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of exchanger thermal substation pipeline/pipeline capacity of Q=150 kW as type XB51H-1-40-2-25-AQ-1G2-1G2, Klase 1. od proizvođača «Danfoss».
With technical characteristics:
Water Primary Secondary
Flow rate m3/h 2.26; 6.62
Temperatures °C / °C 130.0/70.8 90.0 / 70.0
Pressure drop kPa 2 9
Dimensioning pressure bar 25 10
Pipes sizes (DN) 25 50
Total primary pressure drop kPa 36 kPa
Plate material EN 1.4404
Set contains:
- Generic control box, Metal, 3*400V, 1 pump, 401 W to 4 kW
- XB51-40H
- HEX_trans_insu_XB_51 40H_1_1_25_internal_description
- Danfoss, JIP-FF, Ball valve, PN40, DN25, Temp. max 180°C, DN25, Flange, Heating
- Danfoss, FVF - [64], kvs 16.5, PN25, DN25, Temp. max 200°C, DN25, Flange, Heating
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-160°C, L-50mm, Class 2.0, DN15, Welded, Both
- Pocket for thermometer sensor
- Water bag pipe steel DIN 16282/B U-Form angle, G 1/2"
- Danfoss, MDD80, 0-25 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- 3 way valve, 1/2 inch, Suku, Steel, Temp. Max 200C
- Generic muff, 1/2 inch, Inside thread, Both
- IVR, 660, PN25, DN15, Temp. max 200°C, 1/2 inch, Inside thread, Both
- Danfoss, AVQM, kvs 6.3, PN25, DN20, Temp. max 150°C, 1 inch, Outside thread, Heating
- Danfoss, AMV 23, with spring return, no spring up, 230V, Slow
- Generic muff, 1/2 inch, Inside thread, Both
- 3 way valve, 1/2 inch, Suku, Steel, Temp. Max 200C
- Water bag pipe steel DIN 16282/B U-Form angle, G 1/2"
- Danfoss, MDD80, 0-25 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- Pocket for thermometer sensor
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-160°C, L-50mm, Class 2.0, DN15, Welded, Both
- Danfoss, JIP-FF, Ball valve, PN40, DN25, Temp. max 180°C, DN25, Flange, Heating
- 1 " L=190
- Danfoss, JIP-WW, Ball valve, PN40, DN50, Temp. max 180°C, DN50, Welded, Heating
- Pocket for thermometer sensor
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-120°C, L-80mm, Class 2.0, DN15, Welded, Both
- Danfoss, MDD80, 0-10 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- 3 way valve for manometer, 1/2 inch, Tmax=150 C, standard
- Danfoss, FVF - [64], kvs 54, PN16, DN50, Temp. max 150°C, DN50, Flange, Heating
- IVR, 954, PN25, DN15, Temp. max 110°C, 1/2 inch, Inside thread, Both
- IVR, 954, PN25, DN15, Temp. max 110°C, 1/2 inch, Inside thread, Both
- Danfoss, Stainless steel pocket - 100 mm
- Danfoss, ESMU-100/Cu, PN25, Temp. max 140°C, Bo th
- Danfoss, ST-1, Both
- Syr, SYR 1915 DN20 5,5 BAR, max. 5.5 bar, 3/4 ", Inside thread, Both
- WILO, Stratos 30-1-12 (1,37), 1*230V
- 3 way valve for manometer, 1/2 inch, Tmax=150 C, standard
- Danfoss, MDD80, 0-10 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- Pocket for thermometer sensor
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-120°C, L-80mm, Class 2.0, DN15, Welded, Both
- Danfoss, VFY-WH, Butterfly valve, PN16, DN50, Temp. max 120°C, DN50, Inter flange, Heating
- Danfoss, ECL Comfort 110
- Danfoss, ESMT, Both
- Blank box component: Special Pocket for ST1 087N1201 _internal description
- HEX_bracket_XB51H_plates_6-60_internal_description
|  | komplet | 1 | 0
2 | Delivery and installation of closed expansion vessel with membrane with usable volume of 50 liters
|  | pcs | 1 | 0
3 | Delivery and installation of collectors DN100:L=1000mm with 5 pipe conncetros DN40; NP10 in set with accessories for supporting
|  | set | 2 | 0
4 | Delivery and installation of valve for warm water including sealing elements and bolts
| - DN 50 (2“); PN 16; | pcs | 4 | 0
| - DN 32 (5/4”); PN 16; | pcs | 10 | 0
| - DN 25 (1”) ; PN 16; | pcs | 2 | 0
|  | pcs | 2 | 0
5 | Delivery and installation of manometer, p = 0-10bar
6 | Delivery and installation of manometer 1/2", t=20÷150oC,
|  | pcs | 2 | 0
7 | Deliver, transport and installation of seamless steel pipes for the heating system. Inclusive:
- Ф 21,3×2mm (DN 1/2")
| - Ф 33,7×2,6mm (DN 1") | m | 12 | 0
| - Ф 42,4×2,6mm (DN 5/4") | m | 42 | 0
| - Ф 57×2,9mm (DN 2") | m | 84 | 0
|  | m | 12 | 0
8 | Supply and installation of thermal insulation of glass wool layer of aluminum sheet for steel pipe driven into the house, and warm-water channel to the terminal shaft | set
- for pipes fi 2"...............…. 12 m - for pipes fi 5/4".......…..… 84 m - for pipes fi 1".................… 42 m - for pipes fi 1/2".......….... . 12 m
|  |  | 1 | 0
9 | Delivery and installation of steel arches, joints, supports and all other elements needed for making pipe installation (taken cca30% of the sum of the previous items 5 and 6)
|  | All inclusive | 1 | 0
10 | Cleaning, corrosion protection and painting of piping and supports anti-corrosion coatings resistant to elevated temperatures up to 200°C
|  | m2 | 30 | 0
11 | Testing the installation on the strength and tightness in all the technical requirements for pipelines and drafting minutes of testing.
|  | All inclusive | 1 | 0
12 | Marking the pipeline in terms of technological flows, development of functional schemes, instructions for use and maintenance of equipment subject | All inclusive | 1 | 0
13 | Preparatory finishing. This includes transportation and disposal of tools, equipment, crane vehicles and supplies for the safe and efficient performance of the installation work, security personnel and site against unsolicited intervention fails, fire, working at height, and so on.
Total thermal substation and thermal pipline |  |  |  | #REF!
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_17"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_17. (See related scheme 1.4.!) Following equipment have to be installed in main distribution cabinet:
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_17.1 (See related scheme 1.5.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
TOTAL :
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00- 4x70 mm2 (GRO -DO-TS) | m | 100 | 0
| NHXH E60 4x35mm2 | m | 30 | 0
| PPOO 4x16mm2 | m | 15 | 0
| PPOO-Y 5x10 mm2 | m | 15 | 0
| PPOO-Y 5x2,5 mm2 | m | 80 | 0
| PPOO-Y 5x1,5 mm2 | m | 250 | 0
| PPOO-Y 3x2,5 mm2 | m | 80 | 0
| PPOO-Y 1x25 mm2 | m | 55 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 140 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 15 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
TOTAL II :
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 20 | 0
| PNK 200 | m | 30 | 0
| Slat cable carriers 200 mm | m | 30 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 20 | 0
3 | Other small material | flat | 1 | 0
TOTAL III:
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 15 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 5 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 1 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 6 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 11 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 3 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
TOTAL IV :
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 31 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 9 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 20 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 25 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0
| .serial water-proof n/ž | piece | 1 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 2 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 4 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 4 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL V.1 :
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 40 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 40 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 10 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 50 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 3 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL VI:
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 4 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 10 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
TOTAL VII:
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 2 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 6 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 2 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 2 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 30 | 0
| -PP00-Y 3x2,5 mm2 | m. | 6 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 30 | 0
| - PVC warning tape | met | 30 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
TOTAL VIII KM:
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
TOTAL IX:
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 5 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 5 | 0
3. | Protective canopy drip-channel for detector. | piece | 5 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 5 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 5 | 0
7. | Marking elements with persistent marks | piece | 7 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
TOTAL FLAME DETECTORS :
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 9 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 2 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 5 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 3 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 18 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 17 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
18. | Marking elements with persistent marks | piece | 7 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0
TOTAL MANUAL TRANSMITTER
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0
6. | Marking elements with persistant marks | piece | 2 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
TOTAL SIRENS :
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 1 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
TOTAL FLASHES:
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
Creating attests authorized by the domestic industry.
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 4 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 48 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 48 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0
9. | Other unspecified fine material. | m. | 15 | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
TOTAL COMMISSIONING :
TOTAL IX
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 125 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 5 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 5 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 5 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 5 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 5 | 0
Drip:
| KON 21; Rf 200212 | pieces | 7 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 5 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 8 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 18 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 4 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 130 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 110 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 25 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 60 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
TOTAL X :
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS
II) | POWER CABLES
III) | CABLE CARRIERS AND INSTALLATION PIPES
IV) | FLASHLIGHTS
V) | ILIGHTNING INSTALLATION
VI) | OUTLET AND FEEDER INSTALLATIONS
VII) | POTENTIAL EQUALIZING INSTALLATIONS
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE
IX) | FIRE DETECTION SYSTEM
X) | LIGHTNING ROD INSTALLATION
XI) | TESTING AND MESAURING
XII) | PROJECT OF CREATED STATE |  |  | 0
TOTAL

## B-18 MECH
3. BILL OF QUANTITY-HYDRO (B-18)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x1.
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS
1.2 CONCRETE WORKS
1 | Making the connecting shafts of concrete, MB 20 in the corresponding panel. The size and shape of the detail. To carry out treatment on walls and install of creepers. | m3 | 1.1 | 0
1,2x1,2x0,35x1 + 0,8x0,75x1 =
TOTAL 1.2 CONCRETE WORK
1.3. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
3 | Supply and installation of the cover size 80x80 and transport capcacity of 25 tones. Calculation per pieces | psc | 1 | 0
TOTAL 1.3. MASONRY AND BRICKLAYERING WORK
1.4. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 27.91 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 25.46 | 0
Calculation per m of finished work
3 | Supply and installation of flat leaky ball valve Φ 2" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 1 | 0
Calculation per 1 pc. really built on the property.
4 | Supply and installation of flat leaky ball valve Φ 1" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 5 | 0
Calculation per 1 pc. really built on the property.
5 | Supply and installation of ball valves with lever and unions Φ 1 " | psc. | 5 | 0
Calculation per 1 pc. really built on the property.
6 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 53.37 | 0
Calculation per m1 finished work.
TOTAL 1.4. ASSEMBLY WORK
TOTAL 1. PLUMBING
2. SPRINKLER NETWORK
2.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 2,1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for drain line near signal valve, together with the associated fittings according to the plans of the project. Calculation per m of finished work | m1 | 8.26 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for emptying of sprinkler network, together with the associated fittings. Calculation per m of finished work | m1 | 13.17 | 0
3 | Supply and installation of steel galvanized water pipes Φ 1 "(DN25mm), with the connections, for cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 73.04 | 0
4 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN32mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 20.92 | 0
5 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN40mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 0 | 0
6 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 5.23 | 0
7 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 42.8 | 0
8 | Supply and installation of water pipes ducktail Ø 4"together with associated fittings. Calculation per m of finished work. | m1 | 32 | 0
9 | Supply and installation of DUCTIL water pipes Ø 8“ together with associated | m1 | 13 | 0
10 | Supply control valve for the dry signal system on Ø 3“. | psc | 3 | 0
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 3 | 0
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 3 | 0
13 | Supply of gate valve with oval body PN10 DN 80 | psc | 3 | 0
14 | Supply of gate valve with oval body PN10 DN 20 | psc | 1 | 0
15 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network.
|  | psc | 1 | 0
16 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 6.97 | 0
17 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | psc | 1 | 0
18 | Supply and installation of sprinkler Φ1 “ capacity od 0,71 l/s. Calculation per 1 piece really built in building.
|  | psc | 16 | 0
19 | Supply and installation of sprinkler Φ1 “ capacity od 0,50 l/s. Calculation per 1 piece really built in building.
|  | psc | 120 | 0
20 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector). |  | 1 | 0
psc
21 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc.
|  |  | 5 | 0
22 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 217.97 | 0
Calculation per m of finished work.
TOTAL 2.3. ASSEMBLY WORK
TOTAL 2. SPRINKLER NETWORK
3. PRECIPITATOR
3.1. | EARTHWORKS
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 62.84 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 37.44 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 30.04 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 5.36 | 0
TOTAL EARTHWORKS
3.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 2.16 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 7.72 | 0
3 | Fabrication and installation of armor for the bottom plate and walls.
| MC 30 | Kg
| RA 400/500 | Kg
TOTAL CONCRETE WORKS
3.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 12 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | Psc | 4 | 0
| Dim. 80x90 cm | Psc | 4 | 0
| Dim. 80x95 | Psc | 4 | 0
3.3 | TOTAL ASSEMBLY WORK
3 | TOTAL PRECIPITATOR
RECAPITULATION
1. PLUMBING
2.SPRINKLER NETWORK
3. PRECIPITATOR
Total:
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit type KNNL d50 15/12-FM, FTT, RPDTA, KDTA, L, VF***15/12-A, FTT, RPDTA, L, VF (protok 11650 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 210C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 210C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
- section of plate recuperator efficiency min. 60% in summer period
-Empty sections
-Section of ventilator with direct drive, vertical discharge, flow 11620m3/h, external pressure drop 500 Pa
-Flexible connector
Air exhaust part:
- Flexible connector
- Suction section for vertical air intake
- Section of bag filter class F5
- Section of plate recuperator efficiency min. 60% in summer period
- Section of ventilators in anti explosive Ex performance with direct drive, vertical discharge, flow 11620m3/h, external pressure drop 500 Pa
- Blinds for waste air
- Flexible connector
Set
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 56,3 kW at evaporating temperature and the outside temperature 50C to 460C
- 22,8kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
- automatic elements inside air conditioning chamber om antiexplosive design
|  | set | 1 | 0
4 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 1500x1200
- exhaust exterior steel grate
Type AZR/ANŽ-4/3 size 1500x1200
- Diffuser for air supply with a box, model OD-11V/S/I19/Ex
| size 200 | pcs | 1 | 0
size 315
| -air flow regulator MRP-1/Ex in front of OD-11/V | pcs | 1 | 0
Size 200
Size 250
| Pillar box made from stainless steel for air removal from space type LN-3 from two strainers with filter F5 and manual flow regulation | pcs | 4 | 0
| -height h= 2800,connector f 250 | pcs | 15 | 0
-height h= 2800,connector f 250
| -fire damper for all width L= 400 | pcs | 4 | 0
| PL-15 EL120S/A2/T12/Ex-Z | pcs | 15 | 0
dim.200x200
dim.400x300
dim.400x400
| dim.400x500 | pcs | 10 | 0
| dim.400x550 | pcs. | 6 | 0
dim.400x700
dim.450x450
| -Stainless steel suction grid | pcs | 1 | 0
| Size 1200x600 | pcs | 2 | 0
|  | pcs | 1 | 0
|  | pcs | 2 | 0
|  | pcs | 1 | 0
|  | pcs | 2 | 0
|  | pcs | 1 | 0
|  | pcs | 2 | 0
5 | Roof radial ventilator in anti explosive design as at „Clima Celje“ Slovenia
Type EX SVK2-5000/450-4/6,N=1,30/0,90 kW.
Ventilator equipment consists of:
- Elastic connector
- Selfelevating louvers
- flange
- supporting structure for aslope roof in thermal protection
- frequency inverter
set
|  | set | 1 | 0
6 | Galvanized sheet metal ducts of square and circular diameter of plate 0,8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 2100 | 0
7 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
f 160
f 200
|  | m | 20 | 0
|  | m | 60 | 0
8 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 250 | 0
9 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
Total air cinditioning equipment:
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m | pcs
|  |  | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 60 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 14 | 0
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 6 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 9 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 3 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 14 | 0
9 | Small materials for bonding, rosette of pipes, etc. | all inclusive | 1 | 0
10 | Production of civil penetration of pipes 1/2“ (8 pieces) with final processing
11 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
Total equipment for compressed air:
No | An item of bill of quantities – thermal substation and thermal connection - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of exchanger thermal substation pipeline/pipeline capacity of Q=150 kW as type XB51H-1-40-2-25-AQ-1G2-1G2, Klase 1. od proizvođača «Danfoss».
With technical characteristics:
Water Primary Secondary
Flow rate m3/h 2.26; 6.62
Temperatures °C / °C 130.0/70.8 90.0 / 70.0
Pressure drop kPa 2 9
Dimensioning pressure bar 25 10
Pipes sizes (DN) 25 50
Total primary pressure drop kPa 36 kPa
Plate material EN 1.4404
Set contains:
- Generic control box, Metal, 3*400V, 1 pump, 401 W to 4 kW
- XB51-40H
- HEX_trans_insu_XB_51 40H_1_1_25_internal_description
- Danfoss, JIP-FF, Ball valve, PN40, DN25, Temp. max 180°C, DN25, Flange, Heating
- Danfoss, FVF - [64], kvs 16.5, PN25, DN25, Temp. max 200°C, DN25, Flange, Heating
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-160°C, L-50mm, Class 2.0, DN15, Welded, Both
- Pocket for thermometer sensor
- Water bag pipe steel DIN 16282/B U-Form angle, G 1/2"
- Danfoss, MDD80, 0-25 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- 3 way valve, 1/2 inch, Suku, Steel, Temp. Max 200C
- Generic muff, 1/2 inch, Inside thread, Both
- IVR, 660, PN25, DN15, Temp. max 200°C, 1/2 inch, Inside thread, Both
- Danfoss, AVQM, kvs 6.3, PN25, DN20, Temp. max 150°C, 1 inch, Outside thread, Heating
- Danfoss, AMV 23, with spring return, no spring up, 230V, Slow
- Generic muff, 1/2 inch, Inside thread, Both
- 3 way valve, 1/2 inch, Suku, Steel, Temp. Max 200C
- Water bag pipe steel DIN 16282/B U-Form angle, G 1/2"
- Danfoss, MDD80, 0-25 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- Pocket for thermometer sensor
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-160°C, L-50mm, Class 2.0, DN15, Welded, Both
- Danfoss, JIP-FF, Ball valve, PN40, DN25, Temp. max 180°C, DN25, Flange, Heating
- 1 " L=190
- Danfoss, JIP-WW, Ball valve, PN40, DN50, Temp. max 180°C, DN50, Welded, Heating
- Pocket for thermometer sensor
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-120°C, L-80mm, Class 2.0, DN15, Welded, Both
- Danfoss, MDD80, 0-10 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- 3 way valve for manometer, 1/2 inch, Tmax=150 C, standard
- Danfoss, FVF - [64], kvs 54, PN16, DN50, Temp. max 150°C, DN50, Flange, Heating
- IVR, 954, PN25, DN15, Temp. max 110°C, 1/2 inch, Inside thread, Both
- IVR, 954, PN25, DN15, Temp. max 110°C, 1/2 inch, Inside thread, Both
- Danfoss, Stainless steel pocket - 100 mm
- Danfoss, ESMU-100/Cu, PN25, Temp. max 140°C, Bo th
- Danfoss, ST-1, Both
- Syr, SYR 1915 DN20 5,5 BAR, max. 5.5 bar, 3/4 ", Inside thread, Both
- WILO, Stratos 30-1-12 (1,37), 1*230V
- 3 way valve for manometer, 1/2 inch, Tmax=150 C, standard
- Danfoss, MDD80, 0-10 bar, Diameter 80, Class 1,0, 1/2 inch, Outside thread, Both
- Pocket for thermometer sensor
- Danfoss, TDL150, PN40, Aluminium galvanized, 0-120°C, L-80mm, Class 2.0, DN15, Welded, Both
- Danfoss, VFY-WH, Butterfly valve, PN16, DN50, Temp. max 120°C, DN50, Inter flange, Heating
- Danfoss, ECL Comfort 110
- Danfoss, ESMT, Both
- Blank box component: Special Pocket for ST1 087N1201 _internal description
- HEX_bracket_XB51H_plates_6-60_internal_description
|  | set | 1 | 0
2 | Delivery and installation of closed expansion vessel with membrane with usable volume of 50 liters
|  | pcs | 1 | 0
3 | Delivery and installation of collectors DN80:L=1000mm with 5 pipe conncetros DN40; NP10, and 1 pipe conncetros DN50; in set with accessories for supporting and thermal insulation
|  | set | 2 | 0
4 | Delivery and installation of valve for warm water including sealing elements and bolts
- DN 50 (2“); PN 16;
| - DN 32 (5/4”); PN 16; | pcs | 4 | 0
| - DN 25 (1”) ; PN 16; | pcs | 10 | 0
|  | pcs | 2 | 0
5 | Delivery and installation of manometer, p = 0-10bar | pcs | 2 | 0
6 | Delivery and installation of manometer 1/2", t=20÷150oC,
|  | pcs | 2 | 0
7 | Deliver, transport and installation of seamless steel pipes for the heating system. Inclusive:
- Ф 21,3×2mm (DN 1/2")
| - Ф 33,7×2,6mm (DN 1") | m | 12 | 0
| - Ф 42,4×2,6mm (DN 5/4") | m | 42 | 0
| - Ф 57×2,9mm (DN 2") | m | 84 | 0
|  | m | 12 | 0
8 | Supply and installation of thermal insulation of glass wool layer of aluminum sheet for steel pipe driven into the house, and warm-water channel to the terminal shaft | set
- for pipes fi 2"...............…. 12 m - for pipes fi 5/4".......…..… 84 m - for pipes fi 1".................… 42 m - for pipes fi 1/2".......….... . 12 m
|  |  | 1 | 0
9 | Delivery and installation of steel arches, joints, supports and all other elements needed for making pipe installation (taken cca30% of the sum of the previous items 7 and 8)
All inclusive
|  |  | 1 | 0
10 | Cleaning, corrosion protection and painting of piping and supports anti-corrosion coatings resistant to elevated temperatures up to 200°C
|  | m2 | 30 | 0
11 | Testing the installation on the strength and tightness in all the technical requirements for pipelines and drafting minutes of testing.
|  | All inclusive | 1 | 0
12 | Marking the pipeline in terms of technological flows, development of functional schemes, instructions for use and maintenance of equipment subject | All inclusive | 1 | 0
13 | Preparatory finishing. This includes transportation and disposal of tools, equipment, crane vehicles and supplies for the safe and efficient performance of the installation work, security personnel and site against unsolicited intervention fails, fire, working at height, and so on.
Total thermal substation and thermal pipline |  |  |  | #REF!
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_18"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_18. (See related scheme 1.4.!) Following equipment have to be installed in main distribution cabinet:
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_18.1 (See related scheme 1.5.!) Following equipment have to be installed in main distribution cabinet:
| All together | piece | 1 | 0
TOTAL :
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00- 4x70 mm2 (GRO -DO-TS) | m | 100 | 0
| NHXH E60 4x35mm2 | m | 30 | 0
| PPOO 4x16mm2 | m | 15 | 0
| PPOO-Y 5x10 mm2 | m | 15 | 0
| PPOO-Y 5x2,5 mm2 | m | 80 | 0
| PPOO-Y 5x1,5 mm2 | m | 250 | 0
| PPOO-Y 3x2,5 mm2 | m | 80 | 0
| PPOO-Y 1x25 mm2 | m | 55 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 140 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 15 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
TOTAL II :
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 20 | 0
| PNK 200 | m | 30 | 0
| Slat cable carriers 200 mm | m | 30 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 20 | 0
3 | Other small material | flat | 1 | 0
TOTAL III:
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 15 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 5 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 1 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 6 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 11 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 3 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
TOTAL IV :
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 31 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 9 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 20 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 25 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0
| .serial water-proof n/ž | piece | 1 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 2 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 4 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 4 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL V.1 :
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 40 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 40 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 10 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 50 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 3 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL VI:
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 4 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 5 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 10 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
TOTAL VII:
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 2 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 6 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 2 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 2 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 30 | 0
| -PP00-Y 3x2,5 mm2 | m. | 6 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 30 | 0
| - PVC warning tape | met | 30 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
TOTAL VIII KM:
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
TOTAL IX:
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 5 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 5 | 0
3. | Protective canopy drip-channel for detector. | piece | 5 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 5 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 5 | 0
7. | Marking elements with persistent marks | piece | 7 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
TOTAL FLAME DETECTORS :
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 9 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 2 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 5 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 3 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 18 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 17 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
18. | Marking elements with persistent marks | piece | 7 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0
TOTAL MANUAL TRANSMITTER
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0
6. | Marking elements with persistant marks | piece | 2 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
TOTAL SIRENS :
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 1 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
TOTAL FLASHES:
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
Creating attests authorized by the domestic industry.
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 4 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 48 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 48 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0
9. | Other unspecified fine material. | m. | 15 | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
TOTAL COMMISSIONING :
TOTAL IX
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 125 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 5 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 5 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 5 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 5 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 5 | 0
Drip:
| KON 21; Rf 200212 | pieces | 7 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 5 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 8 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 18 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 4 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 130 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 110 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 25 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 60 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
TOTAL X :
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS
II) | POWER CABLES
III) | CABLE CARRIERS AND INSTALLATION PIPES
IV) | FLASHLIGHTS
V) | ILIGHTNING INSTALLATION
VI) | OUTLET AND FEEDER INSTALLATIONS
VII) | POTENTIAL EQUALIZING INSTALLATIONS
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE
IX) | FIRE DETECTION SYSTEM
X) | LIGHTNING ROD INSTALLATION
XI) | TESTING AND MESAURING
XII) | PROJECT OF CREATED STATE
TOTAL

## B-19 MECH
3. BILL OF QUANTITY-HYDRO (B-19)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x2. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS
1.2. CONCRETE WORKS
1 | Making the connecting shafts of concrete, MB 20 in the corresponding panel. The size and shape of the detail. To carry out treatment on walls and install creepers. | m3 | 1.1 | 0
1,2x1,2x0,35x1 + 0,8x0,75x1 =
1.2. TOTAL CONCRETE WORKS
1.3. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
3 | Supply and installation of cover 80x80 and transport capacity 25 tones | kom | 1 | 0
TOTAL 1.3. MASONRY AND BRICKLAYERING WORK
1.4. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN50mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 14.53 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 2.96 | 0
Calculation per m of finished work
3 | Supply and installation of flat leaky ball valve Φ 2" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 2 | 0
Calculation per 1 pc. really built on the property.
4 | Supply and installation of flat leaky ball valve Φ 1" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc | 1 | 0
Calculation per 1 pc. really built on the property.
5 | Supply and installation of ball valves with lever and unions Φ 1 " | psc. | 3 | 0
Calculation per 1 pc. really built on the property.
5 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 17.48 | 0
Calculation per m1 finished work.
TOTAL 1.4. ASSEMBLY WORK
2. SPRINKLER NETWORK
3.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 2,1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for emptying of sprinkler network, together with the associated fittings. Calculation per m of finished work | m1 | 6.44 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for drain line near signal valve according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 4.53 | 0
3 | Supply and installation of steel galvanized water pipes Φ 1 "(DN25mm), with the connections, for cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 15.4 | 0
4 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN32mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 11 | 0
5 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN40mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 4.4 | 0
6 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 12.32 | 0
7 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 4.46 | 0
8 | Supply and installation of water pipes ducktail Ø 4"together with associated fittings. Calculation per m of finished work. | m1 | 9 | 0
9 | Supply and installation of DUCTIL water pipes Ø 8“ together with associated | m1 | 12 | 0
10 | Supply control valve for the dry signal system on Ø 3“. | psc | 2 | 0
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 2 | 0
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 2 | 0
13 | Supply of gate valve with oval body PN10 DN 80 | psc | 2 | 0
14 | Supply of gate valve with oval body PN10 DN 200 | psc | 1 | 0
15 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network.
|  | psc | 1 | 0
16 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 4.65 | 0
17 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | psc | 1 | 0
18 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector).
|  | psc | 1 | 0
19 | Supply and installation of sprinkler Φ1 “ capcity 0,61l/s. Calculation per piece really bult on builiding.
psc
|  |  | 20 | 0
20 | Supply and installation of sprinkler Φ1 “ capcity 0,44l/s. Calculation per piece really bult on builiding.
psc
|  |  | 16 | 0
21 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc. | 2 | 0
23 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 63.2 | 0
Calculation per m of finished work.
TOTAL 2.3. ASSEMBLY WORK
TOTAL 2. SPRINKLER NETWORK
3. PRECIPITATOR
3.1. | EARTHWORKS
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 62.48 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 37.44 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 30.04 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 5.36 | 0
TOTAL EARTHWORKS
3.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 2.16 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 7.72 | 0
3 | Fabrication and installation of armor for the bottom plate and walls. |  | 0 | 0
| MC 30 | Kg | 0 | 0
| RA 400/500 | Kg | 0 | 0
TOTAL CONCRETE WORKS
3.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 12 | 0
2 | Supply and installation of steel covers. |  | 0 | 0
| Dim. 80x80 cm | Psc | 4 | 0
| Dim. 80x90 cm | Psc | 4 | 0
| Dim. 80x95 | Psc | 62.48 | 0
3.3 | TOTAL ASSEMBLY WORK
3 | TOTAL PRECIPITATOR
RECAPITULATION
1. PLUMBING
2.SPRINKLER NETWORK
3.SEWAGE
4. PRECIPITATOR
Total:
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit type tip KNND d50 6/6-FM, FTT, RPDTA, KDTA, L, VF***6/6-A, FTT, RPDTA, L, VF (1770 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
Section of the steam moisturizer with steam generator 20 kg / h
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 950 m3 / h, the external pressure drop 500 Pa
Flexible connection
Drain part:
-Flexible connection
Suction-section of vertical air intake
Section-filtration fabric filter class F5
- section of plate recuperator efficiency min. 60% in summer period
-Section of ventilator with direct drive, vertical discharge in »Ex« execution, flow with two values 2670 m3/h, external pressure drop 500 Pa
-Flexible connector
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 20,0 kW at evaporating temperature 5° and the outside temperature 460C
- 3,6kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
-elements of automation within the air chambers in the explosion-proof design
|  | set | 1 | 0
4 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 650x550
- Exterior exhaust grille of stainless steel
AZR/ANŽ-4/3 type size 650x550
-Nozzle-VŠ-5/315
| -Suction-sift AR-17 with Setting shutter | pcs | 1 | 0
size 355x350
| -Fire-damper wall width L = 250 | pcs | 1 | 0
| PL-15 EL120S/A2/T12/Ex-Z | pcs | 6 | 0
| size 350x300 | pcs | 4 | 0
size 350x300
| -Air-flow control unit | pcs | 3 | 0
size 250x350
|  | pcs | 2 | 0
5 | Galvanized sheet metal ducts 1,00 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 250 | 0
6 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 30 | 0
7 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
Total air conditioning equipment:
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m | pcs
|  |  | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 12 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 6 | 0
5 | Delivery and installation of galvanized steel pipe T pieces- T piece 1/2"
|  | pcs | 2 | 0
6 | Supply and installation of valves for compressed air with connection for flexible hose.
- R 1/2"
|  | pcs | 2 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 1 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 5 | 0
9 | Small materials for bonding, rosette for pipes, etc. | all inclusive | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
| Total equipment for compressed air: |  |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_19"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_19. (See related scheme 1.7.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
TOTAL :
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x35 mm2 (GRO -DO-TS) | m | 50 | 0
| NHXH E60 4x6mm2 | m | 20 | 0
| PPOO 4x16mm2 | m | 20 | 0
| PPOO-Y 5x6 mm2 | m | 12 | 0
| PPOO-Y 5x2,5 mm2 | m | 10 | 0
| PPOO-Y 5x1,5 mm2 | m | 20 | 0
| PPOO-Y 3x2,5 mm2 | m | 10 | 0
| P/F-Y 1x16 mm2 | m | 20 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 40 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 5 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
TOTAL II :
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0
| PNK 200 | m | 25 | 0
| Slat cable carriers 200 mm | m | 25 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 10 | 0
3 | Other small material | flat | 1 | 0
TOTAL III:
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 5 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 2 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 1 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 2 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 2 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 1 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
TOTAL IV :
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 9 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 3 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 10 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 10 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0
| .serial water-proof n/ž | piece | 1 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL V.1 :
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 5 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 5 | 0
3. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 30 | 0
4. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 2 | 0
5. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 2 | 0
6. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 2 | 0
7. | Other small material | flat | 1 | 0
8. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL VI:
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 3 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 3 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 10 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 6 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
TOTAL VII:
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 25 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 3 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 1 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm | m | 30 | 0
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 2 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 45 | 0
| -PP00-Y 3x2,5 mm2 | m. | 13 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 5 | 0
| - PVC warning tape | met | 5 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
TOTAL VIII KM:
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
TOTAL IX:
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 2 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 2 | 0
3. | Protective canopy drip-channel for detector. | piece | 2 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
7. | Marking elements with persistent marks | piece | 2 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
TOTAL FLAME DETECTORS :
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 1 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 2 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 3 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 6 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 6 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 6 | 0
18. | Marking elements with persistent marks | piece | 6 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 3 | 0
TOTAL MANUAL TRANSMITTER
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0
6. | Marking elements with persistant marks | piece | 2 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
TOTAL SIRENS :
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 1 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
TOTAL FLASHES:
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
Creating attests authorized by the domestic industry.
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 4 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 6 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 25 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0
9. | Other unspecified fine material. | m. | 15 | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
TOTAL COMMISSIONING :
TOTAL IX
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 30 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 2 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 2 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 2 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 2 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 2 | 0
Drip:
| KON 21; Rf 200212 | pieces | 4 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 2 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 4 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 4 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 2 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 38 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 40 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 6 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 20 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
TOTAL X :
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS
II) | POWER CABLES
III) | CABLE CARRIERS AND INSTALLATION PIPES
IV) | FLASHLIGHTS
V) | ILIGHTNING INSTALLATION
VI) | OUTLET AND FEEDER INSTALLATIONS
VII) | POTENTIAL EQUALIZING INSTALLATIONS
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE
IX) | FIRE DETECTION SYSTEM
X) | LIGHTNING ROD INSTALLATION
XI) | TESTING AND MESAURING
XII) | PROJECT OF CREATED STATE
| TOTAL |  |  | 0
0

## B-20 MECH
3. BILL OF QUANTITY-HYDRO (B-20)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 5.61 | 0
Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x2. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.48 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 6.16 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 1.2. MASONRY AND BRICKLAYERING WORK
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 28.82 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ 1"(DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 27.72 | 0
Calculation per m of finished work
3 | Supply and installation of steel galvanized water pipes Φ ¾ " (DN20mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for sanitaria. | m1 | 1.05 | 0
Calculation per m of finished work.
4 | Supply and installation of steel galvanized water pipes Φ ½ " (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for sanitaria. | m1 | 1.15 | 0
Calculation per m of finished work.
5 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 5 | 0
Calculation per 1 pc. really built on the property.
6 | Supply and installation of flat leaky ball valve Φ ½ "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 2 | 0
Calculation per 1 pc. really built on the property.
7 | Supply and installation of ball valves with lever and unions Φ 1 " | psc. | 5 | 0
Calculation per 1 pc. really built on the property.
8 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 60.84 | 0
Calculation per m1 finished work.
TOTAL 1.3. ASSEMBLY WORK
1.4 | SANITARY APPLIANCES AND SANITARY WARE
SANITARY APPLIANCES AND ACCESSORIES
Note:
The contractor should offer type and color of the sanitary equipment in agreement with an investor or an architect, and then approach contracting and total access and installation of the same order. Sanitary ware and fittings must be first-class (white), with chrome and feeders, like the type GEBERIT, GROHE, DOLOMITE, LAUFEN or equivalent. Ports-microclimate of supply and sanitary sewers run after approval by investors.
1 | Toilet bowl
Supply and installation of toilet bowls made of first class faience (sanitary ware), white color, and fully functional version with full plastic toilet cover and seat, toilet tank (low mounting) with angle valve and drain in the floor. Calculation per piece of fully installed toilet bowl.
|  | Psc | 1 | 0
2 | Sink
Supply, transmission and assembly of first class faience sink, approx. 55 cm, together with chrome drainage tube and connecting material, one-hand mixer for hot and cold water, and angle valve Ø 1/2 "and all connecting material.
Calculation per piece of fully built sink.
|  | Psc | 1 | 0
3 | Sanitary accessories
Supply and installation of sanitary ware (class I - INOX, or Kimberly-Clark or equivalent) with:
| a) toilet cleaning kit | Psc | 1 | 0
| b) toilet paper holder | Psc | 1 | 0
| c) wall mirror, dimensions 600 x 400 mm, thickness 4 mm, with polished edges | psc | 1 | 0
| d) paper towel holder | Psc
| e) bowl for liquid soap | Psc | 1 | 0
TOTAL:
TOTAL 1.4 SANITARY APPLIANCES AND SANITARY WARE
TOTAL 1. PLUMBING
2. SEWAGE
1.1. EARTHWORKS
1 | Manual excavation of a trench width 80cm in materials of categories III and IV , along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.8 | 0
Calculation per m3 of finished work.
(2x0, 90x0, 6 x12.x12 +1.2) =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3 of finished work.
(2x0, 60x0, 2) =
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1 | 3.08 | 0
Calculation per m3 of finished work.
(2.81 to 0.24) x 1.2) =
TOTAL 2.1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
| Providing drainage pipes to a height of 360 cm from the upper level of the flat roof. | psc | 1 | 0
size 25x25 cm
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3 | ASSEMBLY WORK
Procurement of materials, transportation, installation, thermal insulation, functional and pressure test.
1 | PVC sewer pipes for home sewers.
Supply and installation of PVC sewer pipes for the performance of internal sewage system, according to DIN 8061 and DIN 19531, with all necessary wiring and fittings and small installation material. Perform sealing sewer pipes with rubber rings. Bid to define the exact type of offered sewer, pipes with a certificate that guarantees the quality of pipes and fittings attached. Mandatory sample and approval before making the installation and approved by supervision, by the enrollment in the construction diary. Pipes of dubious quality, without adequate documentation, are forbidden to install. Mandatory photo documentation of built status before backfilling the trench in paragraph 1.1.).
This item includes all the work and all materials, pipe fittings, auxiliary material for joining and fixing - clips for fixed and sliding points.
Calculation per m of built sewers.
| DN 110 | m | 11.8 | 0
| DN 50 | m | 1.65 | 0
2 | PVC sewer revision / sweepers
Supply and installation of PVC sewer audit / sweepers for installation in the bottom of the control shaft AB.
Calculation per piece embedded audit / sweepers.
DN 110
psc
|  |  | 1 | 0
3 | TOP drainage tube
Procurement, supply and installation of the plastic top siphon with horizontal drains diameter Ø50 mm with a grid of stainless steel measuring 150 x 150 mm.
Calculation per piece integrated top siphon.
|  | psc | 1 | 0
4 | PVC ventilation cap
Supply and installation of vertical sewer vent caps, along with copper flashings including a link to waterproof (as type Braas or equivalent). Ventilation cap (set) Ø 50 mm.
Calculation per piece fitted caps.
|  | Psc | 1 | 0
5 | Testing the building sewage
Testing of complete sewage facility with associated buildings pane and header tanks, etc. on the bandwidth and functionality. Testing performed prior to closing pipeline trenches and painting with photographic documentation of the required item 1.1. After successful completion of testing the functionality and impermeability, issue a certificate about the same. Development of rules / instructions on the operation and maintenance of the entire drainage system of the building is included in this item.
Calculation per m of tested network.
|  | m | 13.45 | 0
TOTAL 2.3. ASSEMBLY WORK
TOTAL 2. SEWAGE
3. SPRINKLER NETWORK
3.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 2.1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 2 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3. ASSEMBLY WORK
2 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 16.8 | 0
3 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 79.5 | 0
4 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 65.56 | 0
5 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 31.45 | 0
6 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 98.75 | 0
7 | Supply and installation of water pipes ducktail Ø 4 " together with associated fittings. Calculation per m of finished work. | m1 | 3 | 0
8 | Supply and installation of water pipes ducktail Ø 8"together with associated fittings. Calculation per m of finished work. | m1 | 21 | 0
9 | Supply control valve for the dry signal system on 3. " | psc | 6 | 0
10 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 6 | 0
11 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 6 | 0
12 | Supply of gate valve with oval body PN10 DN 80 | psc | 6 | 0
13 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network. |  |  | 0
0
|  | psc | 1 | 0
14 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 3.6 | 0
15 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | psc | 1 | 0
16 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector).
|  | psc | 1 | 0
17 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc. | 7 | 0
18 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. Really built on the property. | psc. | 7 | 0
19 | Supply and installation of sprinkler Φ1"with capacity of 1,13 l/s Calculation per 1 pc. Really built on the property. | psc | 15 | 0
20 | Supply and installation of sprinkler Φ1"with capacity of 1,09 l/s Calculation per 1 pc. Really built on the property. | psc | 18 | 0
21 | Supply and installation of sprinkler Φ1"with capacity of 0,87 l/s Calculation per 1 pc. Really built on the property. | psc | 75 | 0
22 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 321.85 | 0
Calculation per m of finished work.
TOTAL 3.3. ASSEMBLY WORK
TOTAL 3. SPRINKLER NETWORK
4. PRECIPITATOR
4.1. | EARTHWORKS
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 15.62 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 9.36 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 7.51 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 1.34 | 0
TOTAL EARTHWORKS
4.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 0.54 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 1.93 | 0
3 | Fabrication and installation of armor for the bottom plate and walls.
| MC 30 | Kg
| RA 400/500 | Kg
TOTAL CONCRETE WORKS
4.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 3 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | Psc | 1 | 0
| Dim. 80x90 cm | Psc | 1 | 0
| Dim. 80x95 | Psc | 1 | 0
4.3 | TOTAL ASSEMBLY WORK
4 | TOTAL PRECIPITATOR
RECAPITULATION
1. PLUMBING
2.SPRINKLER NETWORK
3.SEWAGE
4. PRECIPITATOR
Total:
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit type KNND d50 12/9-FM, FTT, RPDTA, KDTA, L, VF***12/9-A, FTT, RPDTA, L,VF (9160 m3/h) product of «Hidria» Slovenia completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 210C
-Winter-design conditions:
Outdoor air: 60C /56% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
- section of ventilator with direct drive, vertical discharge, flow 9160 m3/h, external pressure drop 500 Pa
-Flexible connector
Air exhaust part:
- Flexible connector
- Suction section for vertical air intake
- Section of bag filter class F5
- Section of plate recuperator efficiency min. 60% in summer period
- Section of ventilators in anti explosive Ex performance with direct drive, vertical discharge, flow 9160m3/h, external pressure drop 500 Pa
- Blinds for waste air
- Flexible connector
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 60 kW at evaporating temperature and the outside temperature 50C to 460C
- 30kW heating capacity at outside temperature 0C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
|  | set | 1 | 0
4 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 1250x850
-Exhaust external grid from stainless steel
type AZR/ANŽ-4/3 size 1250x850
| - Diffuser for air supply with a box, model | pcs | 1 | 0
OD-9/KR1/S/I19/Ex in panel 600x600 mm
| Size 310 | pcs | 1 | 0
Size 400
-air flow regulator MRP-1/Ex in front of
| OD-9/S | pcs | 6 | 0
| size 160 | pcs | 5 | 0
size 200
- Diffuser for air supply with a box, model
OD-11V/S/I19/Ex in panel 600x600 mm
| Size 200 | pcs | 6 | 0
| -air flow regulator MRP-1/Ex in front of | pcs | 5 | 0
OD-11V
| size160 | pcs | 8 | 0
-square diffuser for air exhaust KD-16/K/I19 in a panel 600x600 mm
-air flow regulator MRP-1/Ex in front of KD-16/K
size 200
| -fire damper for wall, width L= 400 | pcs | 8 | 0
PL-15 EL120S/A2/T12/Ex-Z
| size800x400 | pcs | 6 | 0
size 600x400
size 500x400
| pillar box made from stainless steel for air removal from rooms type LN-3 from two strainers,with filters class F5 and manual flow regulation | pcs | 6 | 0
-height h= 2800, connector f 250
|  | pcs | 2 | 0
|  | pcs | 2 | 0
|  | pcs | 2 | 0
|  | pcs | 8 | 0
5 | Galvanized sheet metal ducts of square and circular diameter of plate 0.8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 1200 | 0
6 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
f 160
f 200
| f 250 | m | 100 | 0
|  | m | 40 | 0
|  | m | 20 | 0
7 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 200 | 0
8 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
Total air cinditioning equipment:
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m
|  | m | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | pcs | 60 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
|  | pcs | 14 | 0
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 6 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
| - R 1/2" | pca
|  |  | 5 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 4 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2" | all inclusive
|  |  | 15 | 0
9 | Small materials for bonding, rozetne of pipes, etc. | all inclusive | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations
|  | kom | 1 | 0
Total equipment for compressed air: |  |  |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | MAIN DISTRIBUTION CABINET "GRO-B3"
1 | Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks GRO-RO-B20. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet :
Section of grid voltage
1.2. | DISTRIBUTION CABINET "RO.B_20"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_20. (See related scheme 103.2.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
TOTAL :
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x95 mm2 (GRO -DO-TS) | m | 100 | 0
| NHXH E60 4x70 mm2 | m | 30 | 0
| PPOO 4x35mm2 | m | 35 | 0
| PPOO-Y 5x25mm2 | m | 15 | 0
| PPOO-Y 5x16 mm2 | m | 50 | 0
| PPOO-Y 5x10 mm2 | m | 10 | 0
| PPOO-Y 5x6 mm2 | m | 70 | 0
| PPOO-Y 5x4 mm2 | m | 45 | 0
| PPOO-Y 5x2,5 mm2 | m | 25 | 0
| PPOO-Y 5x1,5 mm2 | m | 30 | 0
| PPOO-Y 3x2,5 mm2 | m | 90 | 0
| PPOO-Y 1x70 mm2 | m | 30 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 310 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 18 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
TOTAL II :
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 20 | 0
| PNK 200 | m | 40 | 0
| PNK 300 | m | 45 | 0
| Slat cable carriers 200 mm | m | 40 | 0
| Slat cable carriers 300 mm | m | 45 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 35 | 0
3 | Other small material | flat | 1 | 0
TOTAL III:
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 31 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 9 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 8 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 5 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 6 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 2 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
TOTAL IV :
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 18 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 7 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 50 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 140 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 2 | 0
| .serial water-proof n/ž | piece | 3 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0
| SKX 12/22 Serial switch SMS 03/8 - switch actuator SMO 17/5 - cable gland SPU 25, Type: SKX 12/22, TEP | piece | 1 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 1P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 8 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 3 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 1P+E, enclosure shall begray, Type GHG 511 440 SR 0001, TEP | piece | 8 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 ,Type GHG 511 440 SR 0001, TEP | piece | 3 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL V.1 :
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 60 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 30 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 20 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 80 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 5 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL VI:
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 2 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 10 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 8 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 10 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
TOTAL VII:
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 4 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 140 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 4 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 150 | 0
| -PP00-Y 3x2,5 mm2 | m. | 24 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 150 | 0
| - PVC warning tape | met | 150 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
TOTAL VIII KM:
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
TOTAL IX:
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 8 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 8 | 0
3. | Protective canopy drip-channel for detector. | piece | 8 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 2 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 14 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 6 | 0
7. | Marking elements with persistent marks | piece | 4 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
TOTAL FLAME DETECTORS :
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 5 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
| Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 5 | 0
3 | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 2 | 0
4 | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 5 | 0
5 | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0
6 | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 3 | 0
7. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 4 | 0
8. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
9. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 29 | 0
10. | Supply and delivery of mark elements for the fire alarm system | piece | 22 | 0
11. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
12. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
13. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
14. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
15. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
16. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
17. | Other unspecified fine material. | kpl. | 1 | 0
18. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0
TOTAL MANUAL TRANSMITTER
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain | piece | 1 | 0
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 2 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 2 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 3 | 0
6. | Marking elements with persistant marks | piece | 3 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
TOTAL SIRENS :
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 5 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 2 | 0
5. | Marking elements with persistant marks | piece | 2 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
TOTAL FLASHES:
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 2 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
· 1 piece of the Power supply unit 24V, 5A,
· 1 piece of the rechargeable battery 2x12V, 7,2Ah,
· 1 piece of the automatic fuse 6A,
· relay vard with three relays 24V/2A
· 40 pieces of Two-stairs VS terminals 1.5mm2,
· spaces for safety barriers
· spaces for MDI module
· spaces for SOM module
· 1 piece of the. DIN šina,
· perforated tiles with lid
· other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
Creating attests authorized by the domestic industry.
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 1 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 1 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 23 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box | m | 160 | 0
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 35 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 45 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 40 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 28 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 55 | 0
9. | Other unspecified fine material. | m. | 15 | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
TOTAL COMMISSIONING :
TOTAL IX
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 130 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 5 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 6 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 20 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 5 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 5 | 0
Drip:
| KON 21; Rf 200212 | pieces | 14 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 14 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 7 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 25 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 11 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 11 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 220 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 320 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 44 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 115 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
TOTAL X :
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS
II) | POWER CABLES
III) | CABLE CARRIERS AND INSTALLATION PIPES
IV) | FLASHLIGHTS
V) | ILIGHTNING INSTALLATION
VI) | OUTLET AND FEEDER INSTALLATIONS
VII) | POTENTIAL EQUALIZING INSTALLATIONS
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE
IX) | FIRE DETECTION SYSTEM
X) | LIGHTNING ROD INSTALLATION
XI) | TESTING AND MESAURING
XII) | PROJECT OF CREATED STATE
| TOTAL |  |  | 0
0

## B-21 MECH
3. BILL OF QUANTITY-HYDRO (B-21)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 5.61 | 0
Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x2. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.48 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 6.16 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 1.2. MASONRY AND BRICKLAYERING WORK
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 30.82 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 27.72 | 0
Calculation per m of finished work
3 | Supply and installation of steel galvanized water pipes Φ ¾ " (DN20mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for sanitaria. | m1 | 1.05 | 0
Calculation per m of finished work.
4 | Supply and installation of steel galvanized water pipes Φ ½ " (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for sanitaria. | m1 | 1.15 | 0
Calculation per m of finished work.
5 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 5 | 0
Calculation per 1 pc. really built on the property.
6 | Supply and installation of flat leaky ball valve Φ ½ "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 2 | 0
Calculation per 1 pc. really built on the property.
7 | Supply and installation of ball valves with lever and unions Φ 1 " | psc. | 5 | 0
Calculation per 1 pc. really built on the property.
8 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 60.74 | 0
Calculation per m1 finished work.
TOTAL 1.3. ASSEMBLY WORK
1.4 | SANITARY APPLIANCES AND SANITARY WARE
SANITARY APPLIANCES AND ACCESSORIES
Note:
The contractor should offer type and color of the sanitary equipment in agreement with an investor or an architect, and then approach contracting and total access and installation of the same order. Sanitary ware and fittings must be first-class (white), with chrome and feeders, like the type GEBERIT, GROHE, DOLOMITE, LAUFEN or equivalent. Ports-microclimate of supply and sanitary sewers run after approval by investors.
1 | Toilet bowl
Supply and installation of toilet bowls made of first class faience (sanitary ware), white color, and fully functional version with full plastic toilet cover and seat, toilet tank (low mounting) with angle valve and drain in the floor. Calculation per piece of fully installed toilet bowl.
|  | Psc | 1 | 0
2 | Sink
Supply, transmission and assembly of first class faience sink, approx. 55 cm, together with chrome drainage tube and connecting material, one-hand mixer for hot and cold water, and angle valve Ø 1/2 "and all connecting material.
Calculation per piece of fully built sink.
|  | Psc | 1 | 0
3 | Sanitary accessories
Supply and installation of sanitary ware (class I - INOX, or Kimberly-Clark or equivalent) with:
| a) toilet cleaning kit | Psc | 1 | 0
| b) toilet paper holder | Psc | 1 | 0
| c) wall mirror, dimensions 600 x 400 mm, thickness 4 mm, with polished edges | psc | 1 | 0
| d) paper towel holder | Psc
| e) bowl for liquid soap | Psc | 1 | 0
TOTAL:
TOTAL 1.4 SANITARY APPLIANCES AND SANITARY WARE
TOTAL 1. PLUMBING
2. SEWAGE
1.1. EARTHWORKS
1 | Manual excavation of a trench width 80cm in materials of categories III and IV , along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.8 | 0
Calculation per m3 of finished work.
(2x0, 90x0, 6 x12.x12 +1.2) =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3 of finished work.
(2x0, 60x0, 2) =
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1 | 3.08 | 0
Calculation per m3 of finished work.
(2.81 to 0.24) x 1.2) =
TOTAL 2.1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
| Providing drainage pipes to a height of 360 cm from the upper level of the flat roof. | psc | 1 | 0
size 25x25 cm
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3 | ASSEMBLY WORK
Procurement of materials, transportation, installation, thermal insulation, functional and pressure test.
1 | PVC sewer pipes for home sewers.
Supply and installation of PVC sewer pipes for the performance of internal sewage system, according to DIN 8061 and DIN 19531, with all necessary wiring and fittings and small installation material. Perform sealing sewer pipes with rubber rings. Bid to define the exact type of offered sewer, pipes with a certificate that guarantees the quality of pipes and fittings attached. Mandatory sample and approval before making the installation and approved by supervision, by the enrollment in the construction diary. Pipes of dubious quality, without adequate documentation, are forbidden to install. Mandatory photo documentation of built status before backfilling the trench in paragraph 1.1.).
This item includes all the work and all materials, pipe fittings, auxiliary material for joining and fixing - clips for fixed and sliding points.
Calculation per m of built sewers.
| DN 110 | m | 11.8 | 0
| DN 50 | m | 1.65 | 0
2 | PVC sewer revision / sweepers
Supply and installation of PVC sewer audit / sweepers for installation in the bottom of the control shaft AB.
Calculation per piece embedded audit / sweepers.
DN 110
psc
|  |  | 1 | 0
3 | TOP drainage tube
Procurement, supply and installation of the plastic top siphon with horizontal drains diameter Ø50 mm with a grid of stainless steel measuring 150 x 150 mm.
Calculation per piece integrated top siphon.
|  | psc | 1 | 0
4 | PVC ventilation cap
Supply and installation of vertical sewer vent caps, along with copper flashings including a link to waterproof (as type Braas or equivalent). Ventilation cap (set) Ø 50 mm.
Calculation per piece fitted caps.
|  | Psc | 1 | 0
5 | Testing the building sewage
Testing of complete sewage facility with associated buildings pane and header tanks, etc. on the bandwidth and functionality. Testing performed prior to closing pipeline trenches and painting with photographic documentation of the required item 1.1. After successful completion of testing the functionality and impermeability, issue a certificate about the same. Development of rules / instructions on the operation and maintenance of the entire drainage system of the building is included in this item.
Calculation per m of tested network.
|  | m | 13.45 | 0
TOTAL 2.3. ASSEMBLY WORK
TOTAL 2. SEWAGE
3. SPRINKLER NETWORK
3.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 2.1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 2 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for line which is supplying fountains for washing according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 21.75 | 0
2 | Supply and installation of steel galvanized water pipes Φ 2 " (DN32mm), with the connections, for line which is supplying fountains for washing according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 28.82 | 0
3 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, for drain lines near signal valve according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 20.1 | 0
4 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, for line for emptying of sprinkler network according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 18.6 | 0
5 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 64 | 0
6 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 48 | 0
7 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 32.16 | 0
8 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 91 | 0
9 | Supply and installation of water pipes ducktail Ø 8"together with associated fittings. Calculation per m of finished work. | m1 | 21 | 0
10 | Supply control valve for the dry signal system on 3. " | psc | 6 | 0
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 6 | 0
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 6 | 0
13 | Supply of gate valve with oval body PN10 DN 80 | psc | 6 | 0
14 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network. |  |  | 0
0
|  | psc | 1 | 0
15 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 3.6 | 0
16 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | psc | 1 | 0
17 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector).
|  | psc | 1 | 0
18 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc. | 6 | 0
19 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. Really built on the property. | psc. | 6 | 0
20 | Supply and installation of sprinkler Φ1"with capacity of 0,87 l/s Calculation per 1 pc. Really built on the property. | psc | 150 | 0
21 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 321.01 | 0
Calculation per m of finished work.
TOTAL 3.3. ASSEMBLY WORK
TOTAL 3. SPRINKLER NETWORK
4. PRECIPITATOR
4.1. | EARTHWORKS
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 31.24 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 18.72 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 15.02 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 2.68 | 0
TOTAL EARTHWORKS
4.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 1.08 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 3.86 | 0
3 | Fabrication and installation of armor for the bottom plate and walls. |  | 31.24 | 0
| MC 30 | Kg
| RA 400/500 | Kg
TOTAL CONCRETE WORKS
4.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 6 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | Psc | 2 | 0
| Dim. 80x90 cm | Psc | 2 | 0
| Dim. 80x95 | Psc | 2 | 0
4.3 | TOTAL ASSEMBLY WORK
4 | TOTAL PRECIPITATOR
RECAPITULATION
1. PLUMBING
2.SPRINKLER NETWORK
3.SEWAGE
4. PRECIPITATOR
Total:
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit type KNND d50 12/9-FM, FTT, RPDTA, KDTA, L, VF***12/9-A, FTT, RPDTA, L,VF (8950 m3/h) product of «Hidria» Slovenia complitely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 210C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 210C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
- section of plate recuperator efficiency min. 60% in summer period
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of8950m3 / h, the external pressure drop 500 Pa
-Flexible connection
Air exhaust part:
- Flexible connector
- Suction section for vertical air intake
- Section of bag filter class F5
- Section of plate recuperator efficiency min. 60% in summer period
- Section of ventilators in anti explosive Ex performance with direct drive, vertical discharge, flow 8950 m3/h, external pressure drop 500 Pa
- Blinds for waste air
- Flexible connector
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 55 kW at evaporating temperature and the outside temperature 50C to 460C
- 30kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | kompl | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
|  | kompl | 1 | 0
4 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 1250x850
-exhaust exterior steel grate
type AZR/ANŽ-4/3 size 1250x850
- Diffuser for air supply with a box, model
| OD-11V/S/I19/Ex in a panel 600x600 mm | pcs | 1 | 0
Size 250
| Air flow regulator MRP-1/Ex in front of OD-11/V | pcs | 1 | 0
Size 200
-square diffusor for air exhaust KD-15/K/I19 in a a panel 600x600 mm
| Air flow regulator MRP-1/Ex in front of | pcs | 24 | 0
KD-15
| size 200 | pcs | 24 | 0
-fire damper for wall, width L= 400
| PL-15 EL120S/A2/T12/Ex-Z | pcs | 1 | 0
size400x200
size.500X400
| size700X400 | pcs | 1 | 0
Pillar box made from stainless steel for removal of air from space type LN-3 from two strainers with filter F5 and manual flow regulation
-height h= 2800,connector f 250
|  | pcs | 2 | 0
|  | pcs | 2 | 0
|  | pcs | 2 | 0
|  | pcs | 12 | 0
6 | Galvanized sheet metal ducts of square and circular diameter of plate 1.00 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 950 | 0
7 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
f 160
f 250
|  | m | 60 | 0
|  | m | 60 | 0
8 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 150 | 0
| Fine regulation, commissioning, testing capacity and quantity. | comissioning
|  |  | 1 | 0
Total air cinditioning equipment:
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Jedinica | Količina | Ukupna
|  | mjere |  | cijena
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m
|  | pcs | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 60 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
|  | pcs | 14 | 0
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 9 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 7 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 6 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 15 | 0
9 | Small materials for bonding, rozetne of pipes, etc. | all inclusive | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
| Total equipment for compressed air: |  |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_21"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_21. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
TOTAL :
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x95 mm2 (GRO -DO-TS) | m | 100 | 0
| NHXH E60 4x50 mm2 | m | 30 | 0
| PPOO-Y 5x25mm2 | m | 15 | 0
| PPOO-Y 5x16 mm2 | m | 10 | 0
| PPOO-Y 5x10 mm2 | m | 10 | 0
| PPOO-Y 5x2,5 mm2 | m | 25 | 0
| PPOO-Y 5x1,5 mm2 | m | 30 | 0
| PPOO-Y 3x2,5 mm2 | m | 90 | 0
| PPOO-Y 1x50 mm2 | m | 30 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 320 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 20 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
TOTAL II :
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 25 | 0
| PNK 200 | m | 70 | 0
| PNK 300 | m | 50 | 0
| Slat cable carriers 200 mm | m | 70 | 0
| Slat cable carriers 300 mm | m | 50 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 40 | 0
3 | Other small material | flat | 1 | 0
TOTAL III:
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 36 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 5 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 10 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 6 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 2 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 2 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
TOTAL IV :
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 17 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 7 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 50 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 120 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 2 | 0
| .serial water-proof n/ž | piece | 2 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0
| SKX 12/22 Serial switch SMS 03/8 - switch actuator SMO 17/5 - cable gland SPU 25, Type: SKX 12/22, TEP | piece | 1 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 1P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 9 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 2 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 1P+E, enclosure shall begray, Type GHG 511 440 SR 0001, TEP | piece | 1 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL V.1 :
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 100 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 20 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 30 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 100 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 5 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL VI:
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 2 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 10 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 8 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 10 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
TOTAL VII:
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 4 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 140 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm | piece | 4 | 0
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 4 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 150 | 0
| -PP00-Y 3x2,5 mm2 | m. | 24 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 150 | 0
| - PVC warning tape | met | 150 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
TOTAL VIII KM:
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
TOTAL IX:
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 6 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 6 | 0
3. | Protective canopy drip-channel for detector. | piece | 6 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 2 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 12 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 6 | 0
7. | Marking elements with persistent marks | piece | 4 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
TOTAL FLAME DETECTORS :
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 9 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
| Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 5 | 0
3 | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 2 | 0
4 | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 5 | 0
5 | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0
6 | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 3 | 0
7. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 4 | 0
8. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
9. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 23 | 0
10. | Supply and delivery of mark elements for the fire alarm system | piece | 22 | 0
11. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
12. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
13. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
14. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
15. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
16. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
17. | Other unspecified fine material. | kpl. | 1 | 0
18. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0
TOTAL MANUAL TRANSMITTER
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain | piece | 1 | 0
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 2 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 2 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 3 | 0
6. | Marking elements with persistant marks | piece | 3 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
TOTAL SIRENS :
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 4 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 2 | 0
5. | Marking elements with persistant marks | piece | 2 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
TOTAL FLASHES:
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 2 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
· 1 piece of the Power supply unit 24V, 5A,
· 1 piece of the rechargeable battery 2x12V, 7,2Ah,
· 1 piece of the automatic fuse 6A,
· relay vard with three relays 24V/2A
· 40 pieces of Two-stairs VS terminals 1.5mm2,
· spaces for safety barriers
· spaces for MDI module
· spaces for SOM module
· 1 piece of the. DIN šina,
· perforated tiles with lid
· other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
Creating attests authorized by the domestic industry.
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 1 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 1 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 25 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box | m | 140 | 0
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 40 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 50 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 45 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 20 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 55 | 0
9. | Other unspecified fine material. | m. | 15 | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
TOTAL COMMISSIONING :
TOTAL IX
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 200 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 6 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 6 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 25 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 6 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 7 | 0
Drip:
| KON 21; Rf 200212 | pieces | 8 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 5 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 8 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 13 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 11 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 11 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 220 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 320 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 44 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 115 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
TOTAL X :
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS
II) | POWER CABLES
III) | CABLE CARRIERS AND INSTALLATION PIPES
IV) | FLASHLIGHTS
V) | ILIGHTNING INSTALLATION
VI) | OUTLET AND FEEDER INSTALLATIONS
VII) | POTENTIAL EQUALIZING INSTALLATIONS
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE
IX) | FIRE DETECTION SYSTEM
X) | LIGHTNING ROD INSTALLATION
XI) | TESTING AND MESAURING
XII) | PROJECT OF CREATED STATE
| TOTAL |  |  | 0

## B-22 MECH
3. BILL OF QUANTITY-HYDRO (B-22)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.81 | 0
Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x2. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS
1.2. CONCRETE WORKS
1 | Making the connecting shafts of concrete, MB 20 in the corresponding panel. The size and shape of the detail. To carry out treatment on walls and install creepers. | m3 | 1.1 | 0
1,2x1,2x0,35x1 + 0,8x0,75x1 =
1.2. TOTAL CONCRETE WORKS
1.3. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
3 | Supply and installation of cover 80x80 and transport capacity 25 tones | pcs | 1 | 0
TOTAL 1.3. MASONRY AND BRICKLAYERING WORK
1.4. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 40.01 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 10.15 | 0
Calculation per m of finished work
3 | Supply and installation of flat leaky ball valve Φ 2" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 1 | 0
Calculation per 1 pc. really built on the property.
4 | Supply and installation of flat leaky ball valve Φ 1“ on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | Psc. | 5 | 0
Calculation per 1 pc. really built on the property.
5 | Supply and installation of ball valves with lever and unions Φ 1 " | psc. | 5 | 0
Calculation per 1 pc. really built on the property.
6 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 50.16 | 0
Calculation per m1 finished work.
TOTAL 1.4. ASSEMBLY WORK
2. SPRINKLER NETWORK
2.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 2,1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 2 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for emptying of sprinkler network, together with the associated fittings. Calculation per m of finished work | m1 | 18.45 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 " (DN32mm), with the connections, for drain line near signal valve according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 10.7 | 0
3 | Supply and installation of steel galvanized water pipes Φ 1 "(DN25mm), with the connections, for cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work | m1 | 50.78 | 0
4 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN32mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 38.18 | 0
5 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN40mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 12.74 | 0
6 | Supply and installation of galvanized steel plumbing Φ 2 "(DN50mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work | m1 | 4.43 | 0
7 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 15.03 | 0
8 | Supply and installation of water pipes ducktail Ø 4"together with associated fittings. Calculation per m of finished work. | m1 | 77 | 0
9 | Supply and installation of DUCTIL water pipes Ø 8“ together with associated | m1 | 14 | 0
10 | Supply control valve for the dry signal system on Ø 4“. | psc | 5 | 0
11 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | psc | 5 | 0
12 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | psc | 5 | 0
13 | Supply of gate valve with oval body PN10 DN 80 | psc | 5 | 0
14 | Supply of gate valve with oval body PN10 DN 200 | psc | 1 | 0
15 | Supply and installation of non-return valve diameter Ø 8 " at the inlet line for sprinkler network.
|  | psc | 1 | 0
16 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 2.36 | 0
17 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | psc | 1 | 0
18 | Supply and installation of sprinkler Φ1" with capacity of 0,47l/s Calculation per 1 pc. Really built on the property. | pcs | 85 | 0
19 | Supply and installation of sprinkler Φ1" with capacity of 0,56l/s Calculation per 1 pc. Really built on the property. | pcs | 30 | 0
20 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector). |  | 1 | 0
psc
21 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property.. | psc. | 5 | 0
22 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 167.38 | 0
Calculation per m of finished work.
TOTAL 3.3. ASSEMBLY WORK
TOTAL 3. SPRINKLER NETWORK
4. PRECIPITATOR
4.1. | EARTHWORKS
1 | Excavation category III countries, machine way at depth of 0-3.5 m rejection from the country at a distance 1.0 m from the edge of the excavation. | m3 | 62.48 | 0
2 | Backfilling excavated soil septic, with compacting in layers of 30 cm. | m3 | 37.44 | 0
3 | Removal of excess soil to the landfill with spreading and leveling the dump. | m3 | 30.04 | 0
(15.62 to 9.36) x 1, 20
4 | Supply, filling and compacting gravel for the bottom plate surface sewage in thickness from 20 cm | m3 | 5.36 | 0
TOTAL EARTHWORKS
4.2 | CONCRETE WORKS
1 | Making septic bottom plate from the reinforced concrete MB 30. | m3 | 2.16 | 0
2 | Making walls from the-reinforced concrete MB 30. Walls width d=15 cm. Making the double-sided plate. | m3 | 7.72 | 0
3 | Fabrication and installation of armor for the bottom plate and walls.
| MC 30 | Kg
| RA 400/500 | Kg
TOTAL CONCRETE WORKS
4.3. | ASSEMBLY WORK
1 | Supply and installation of PVC pipes and fittings Ø 200 | Psc | 12 | 0
2 | Supply and installation of steel covers.
| Dim. 80x80 cm | Psc | 4 | 0
| Dim. 80x90 cm | Psc | 4 | 0
| Dim. 80x95 | Psc | 4 | 0
4.3 | TOTAL ASSEMBLY WORK
4 | TOTAL PRECIPITATOR
RECAPITULATION
1. PLUMBING
2.SPRINKLER NETWORK
3.SEWAGE
4. PRECIPITATOR
Total:
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit type KNND d50 9/9-FM, FTT, RPDTA, KDTA, L, VF***9/9-A, FTT, RPDTA, L, VF (6150 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
- section of plate recuperator efficiency min. 60% in summer period
-Empty sections
-Section of ventilator with direct drive, vertical discharge, flow with two values 7200/ 2150 m3/h, external pressure drop 500 Pa
-Flexible connector
Air exhaust part:
- Flexible connector
- Suction section for vertical air intake
- Section of bag filter class F5
- Section of plate recuperator efficiency min. 60% in summer period
- Section of ventilators in anti explosive Ex performance with direct drive, vertical discharge, flow 7200/2150 m3/h, external pressure drop 500 Pa
- Blinds for waste air
- Flexible connector
Set
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 40 kW at evaporating temperature and the outside temperature 50C to 460C
- 35kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
|  | set | 1 | 0
4 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 950x850
- exhaust exterior steel grate
Type AZR/ANŽ-4/3 size 950x850
- Diffuser for air supply with a box, model OD-11V/S/I19/Ex
| size 200 | pcs | 1 | 0
size 355
| -air flow regulator MRP-1/Ex in front of OD-11/V | pcs | 1 | 0
Size 160
Size 200
| -fire damper for all width L= 400 | pcs | 8 | 0
| PL-15 EL120S/A2/T12/Ex-Z | pcs | 8 | 0
Size 700x400
| Size 550x400 | pcs | 8 | 0
| Size 400x300 | pcs | 8 | 0
Pillar box made from stainless steel for air removal from space type LN-3 from two strainers with filter F5 and manual flow regulation
-height h= 3600,connector f 250
|  | pcs | 4 | 0
|  | pcs. | 4 | 0
|  | pcs | 2 | 0
|  | pcs | 8 | 0
5 | Galvanized sheet metal ducts of square and circular diameter of plate 1.00 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 1350 | 0
6 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 200 | 0
7 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
f 160
f 200
|  | m | 40 | 0
|  | m | 40 | 0
8 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
Total air cinditioning equipment:
No | An item of bill of quantities - equipment for compressed air - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Delivery and installation of rotary screw compressors as type CSM 5.5 X MINI product CECCATO, with following technical characteristics:
- Model type CSM 5,5 X MINI,
- Air pressure up to 10 bar (145 psi),
- Power 4 kW (5,5 HP),
- Flow 470 lit/min 28,2 m2/h,
- Noise level 62 dB
- Power supply 400/50/3 V/hz/Ph
- Bowl volume 300 (lit)
|  | set | 1 | 0
2 | The docking reinforced flexible hose with couplings 1/2" L=1m | pcs
|  |  | 1 | 0
3 | Delivery and installation of galvanized steel pipes- 1/2"
|  | m | 60 | 0
4 | Delivery and installation of galvanized steel pipe arches - 1/2"
pcs
|  |  | 14 | 0
5 | Delivery and installation of galvanized steel pipeT pieces- T piece 1/2"
|  | pcs | 9 | 0
6 | Supply and installation of valves for compressed air with connection for flxible hose.
- R 1/2"
|  | pcs | 6 | 0
7 | Supply and installation of a flexible hose for air, length 10m in a set, rolled on a circular holder.
|  | pcs | 5 | 0
8 | Supply and installation of holders- single clamps for pipe 1/2"
|  | pcs | 15 | 0
9 | Small materials for bonding, rozetne of pipes, etc. | all inclusive | 1 | 0
10 | Pressure test the strength and tightness of compressed air installations | all inclusive
|  |  | 1 | 0
Total equipment for compressed air:
0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_22"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_22. (See related scheme 1.4.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
TOTAL :
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00- 4x35 mm2 (GRO -DO-TS) | m | 100 | 0
| PPOO 4x16mm2 | m | 15 | 0
| NHXH E60 4x6mm2 | m | 15 | 0
| PPOO-Y 5x4 mm2 | m | 15 | 0
| PPOO-Y 5x2,5 mm2 | m | 5 | 0
| PPOO-Y 5x1,5 mm2 | m | 100 | 0
| PPOO-Y 3x2,5 mm2 | m | 180 | 0
| PPOO-Y 1x16 mm2 | m | 15 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 150 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 15 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
TOTAL II :
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 5 | 0
| PNK 200 | m | 30 | 0
| Slat cable carriers 200 mm | m | 30 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 10 | 0
3 | Other small material | flat | 1 | 0
TOTAL III:
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 21 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 3 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 1 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 5 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 12 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 1 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
TOTAL IV :
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 36 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 6 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 25 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 25 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0
| .serial water-proof n/ž | piece | 2 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 2 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 2 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 2 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL V.1 :
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 10 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 10 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 20 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 2 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 2 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 2 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL VI:
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 3 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 4 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 9 | 0
6 | Creating bypass Gauge | piece | 2 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
TOTAL VII:
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 2 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 6 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 2 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 2 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 30 | 0
| -PP00-Y 3x2,5 mm2 | m. | 6 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 30 | 0
| - PVC warning tape | met | 30 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
TOTAL VIII KM:
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
TOTAL IX:
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 5 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 5 | 0
3. | Protective canopy drip-channel for detector. | piece | 5 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 5 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 5 | 0
7. | Marking elements with persistent marks | piece | 5 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
TOTAL FLAME DETECTORS :
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 6 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 2 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 5 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 1 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 20 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 12 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 1 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
18. | Marking elements with persistent marks | piece | 7 | 0
19. | Other unspecified fine material. | kpl. | 1 | 0
20. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0
TOTAL MANUAL TRANSMITTER
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0
6. | Marking elements with persistant marks | piece | 2 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
TOTAL SIRENS :
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 1 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
TOTAL FLASHES:
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
Creating attests authorized by the domestic industry.
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 30 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 60 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 60 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 20 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0
9. | Other unspecified fine material. | m. | 15 | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
| . Handover and assembling the record on safety and functional testing. |  |  | 0
TOTAL COMMISSIONING :
TOTAL IX
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 120 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 6 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 6 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 6 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 6 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 6 | 0
Drip:
| KON 21; Rf 200212 | pieces | 6 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 5 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 6 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 6 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 6 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 125 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 240 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 40 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 90 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
TOTAL X :
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS
II) | POWER CABLES
III) | CABLE CARRIERS AND INSTALLATION PIPES
IV) | FLASHLIGHTS
V) | ILIGHTNING INSTALLATION
VI) | OUTLET AND FEEDER INSTALLATIONS
VII) | POTENTIAL EQUALIZING INSTALLATIONS
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE
IX) | FIRE DETECTION SYSTEM
X) | LIGHTNING ROD INSTALLATION
XI) | TESTING AND MESAURING
XII) | PROJECT OF CREATED STATE
| TOTAL |  |  | 0
0

## B-23 MECH
3. BILL OF QUANTITY-HYDRO (B-23)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
1.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 5.61 | 0
Calculation per m3 of finished work. (2x0,90x0,6+1.2x12.x12)x2. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.48 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 6.16 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 1.2. MASONRY AND BRICKLAYERING WORK
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1"(DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 29.4 | 0
Calculation per m of finished work
1 | Supply and installation of steel galvanized water pipes Φ ¾ " (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 1.1 | 0
Calculation per m of finished work.
1 | Supply and installation of steel galvanized water pipes Φ ½ " (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 4.2 | 0
Calculation per m of finished work.
2 | Supply and installation of flat leaky ball valve Φ 1 "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | pcs | 3 | 0
Calculation per 1 pc. really built on the property.
2 | Supply and installation of flat leaky ball valve Φ ½ "on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | pcs | 8 | 0
Calculation per 1 pc. really built on the property.
3 | Supply and installation of ball valves with lever and unions Φ 1 " | pcs | 1 | 0
Calculation per 1 pc. really built on the property.
5 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 34.7 | 0
Calculation per m1 finished work.
TOTAL 1.3. ASSEMBLY WORK
1.4 | SANITARY APPLIANCES AND SANITARY WARE
SANITARY APPLIANCES AND ACCESSORIES
Note:
The contractor should offer type and color of the sanitary equipment in agreement with an investor or an architect, and then approach contracting and total access and installation of the same order. Sanitary ware and fittings must be first-class (white), with chrome and feeders, like the type GEBERIT, GROHE, DOLOMITE, LAUFEN or equivalent. Ports-microclimate of supply and sanitary sewers run after approval by investors.
1 | Toilet bowl
Supply and installation of toilet bowls made of first class faience (sanitary ware), white color, and fully functional version with full plastic toilet cover and seat, toilet tank (low mounting) with angle valve and drain in the floor. Calculation per piece of fully installed toilet bowl.
|  | pcs | 2 | 0
2 | Sink
Supply, transmission and assembly of first class faience sink, approx. 55 cm, together with chrome drainage tube and connecting material, one-hand mixer for hot and cold water, and angle valve Ø 1/2 "and all connecting material.
Calculation per piece of fully built sink.
|  | pcs | 4 | 0
3 | Sanitary accessories
Supply and installation of sanitary ware (class I - INOX, or Kimberly-Clark or equivalent) with:
| a) toilet cleaning kit | pcs | 2 | 0
| b) toilet paper holder | pcs | 2 | 0
| c) wall mirror, dimensions 600 x 400 mm, thickness 4 mm, with polished edges | pcs | 2 | 0
| d) paper towel holder | pcs | 2 | 0
| e) bowl for liquid soap | pcs | 2 | 0
TOTAL:
TOTAL 1.4 SANITARY APPLIANCES AND SANITARY WARE
TOTAL 1. PLUMBING
2. SEWAGE
1.1. EARTHWORKS
1 | Manual excavation of a trench width 80cm in materials of categories III and IV , along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.8 | 0
Calculation per m3 of finished work.
(2x0, 90x0, 6 x12.x12 +1.2) =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3 of finished work.
(2x0, 60x0, 2) =
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m3 | 3.08 | 0
Calculation per m3 of finished work.
(2.81 to 0.24) x 1.2) =
TOTAL 2.1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
| Providing drainage pipes to a height of 360 cm from the upper level of the flat roof. | pcs | 1 | 0
size 25x25 cm
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3 | ASSEMBLY WORK
Procurement of materials, transportation, installation, thermal insulation, functional and pressure test.
1 | PVC sewer pipes for home sewers.
Supply and installation of PVC sewer pipes for the performance of internal sewage system, according to DIN 8061 and DIN 19531, with all necessary wiring and fittings and small installation material. Perform sealing sewer pipes with rubber rings. Bid to define the exact type of offered sewer, pipes with a certificate that guarantees the quality of pipes and fittings attached. Mandatory sample and approval before making the installation and approved by supervision, by the enrollment in the construction diary. Pipes of dubious quality, without adequate documentation, are forbidden to install. Mandatory photo documentation of built status before backfilling the trench in paragraph 1.1.).
This item includes all the work and all materials, pipe fittings, auxiliary material for joining and fixing - clips for fixed and sliding points.
Calculation per m of built sewers.
| DN 110 | m | 14.45 | 0
| DN 50 | m | 6.5 | 0
2 | PVC sewer revision / sweepers
Supply and installation of PVC sewer audit / sweepers for installation in the bottom of the control shaft AB.
Calculation per piece embedded audit / sweepers.
DN 110
pcs
|  |  | 1 | 0
3 | TOP drainage tube
Procurement, supply and installation of the plastic top siphon with horizontal drains diameter Ø50 mm with a grid of stainless steel measuring 150 x 150 mm.
Calculation per piece integrated top siphon.
|  | pcs | 2 | 0
4 | PVC ventilation cap
Supply and installation of vertical sewer vent caps, along with copper flashings including a link to waterproof (as type Braas or equivalent). Ventilation cap (set) Ø 50 mm.
Calculation per piece fitted caps.
|  | pcs | 1 | 0
5 | Testing the building sewage
Testing of complete sewage facility with associated buildings pane and header tanks, etc. on the bandwidth and functionality. Testing performed prior to closing pipeline trenches and painting with photographic documentation of the required item 1.1. After successful completion of testing the functionality and impermeability, issue a certificate about the same. Development of rules / instructions on the operation and maintenance of the entire drainage system of the building is included in this item.
Calculation per m of tested network.
|  | m | 20.95 | 0
TOTAL 2.3. ASSEMBLY WORK
TOTAL 2. SEWAGE
3. SPRINKLER NETWORK
3.1. EARTHWORKS
The calculation is performed at plumbing works, because the installation of water and hydrant network is laid in the same trench.
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3
Calculation per m3 of finished work.
2 | Development of the placenta from the sand, along with planning and compaction. | m3
Calculation per m3 of finished work.
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1
Calculation per m3 of finished work.
TOTAL 2.1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking openings in slabs and walls for the incursions of sewer pipes along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 2 | 0
| Calculation per piece. | Kom
2 | Slice consuming breaking in slabs and walls for laying sewer pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK
2.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the connections, cold water according to the plans of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 86.25 | 0
2 | Supply and installation of steel galvanized water pipes Φ 1 "(DN32mm), with the development of compounds for the exhaust valve signal line at the designs of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 21 | 0
3 | Supply and installation of galvanized steel plumbing Φ 5/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 63.35 | 0
4 | Supply and installation of galvanized steel plumbing Φ 6/4 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 15.4 | 0
5 | Supply and installation of galvanized steel plumbing Φ 2 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m of finished work. | m1 | 11.89 | 0
6 | Supply and installation of galvanized steel plumbing Φ 3 "(DN25mm), with the development of compounds for cold water according to the design of the project, together with the associated fittings. Calculation per m3 of finished work. | m1 | 22.58 | 0
7 | Supply and installation of water pipes ducktail Ø 6 "together with associated fittings. Calculation per m of finished work. | m1 | 126.75 | 0
8 | Supply control valve for the wet signal system on 3. " | pcs | 3 | 0
9 | Supply of mechanical devices for fire alarm systems (purchase bundled with valve control signal). | pcs | 3 | 0
10 | Supply of electrical signaling devices (purchase bundled with the valve control signal). | pcs | 3 | 0
11 | Supply of gate valve with oval body PN10 DN 80 | pcs | 6 | 0
12 | Supply and installation of non-return valve diameter 6 " at the inlet line for sprinkler network.
|  | pcs | 1 | 0
13 | Building supply lines for fire engines from DUCTIL tube Ø 3 " | m | 13.3 | 0
14 | Supply and installation of non-return valve Ø 3 „at the inlet lines for fire trucks.
|  | pcs | 1 | 0
15 | Supply and installation of connectors for connection Ø 3” fire engines (double type connector).
|  | pcs | 1 | 0
16 | Supply and installation of flat leaky ball valve Φ 1"in some trace distribution of cold water and functioning trial. Valves are supplied with a chrome handle for opening and decorative chrome bezel. Calculation per 1 piece that is really built on the property. | pcs | 10 | 0
17 | Supply and installation of ball valves with lever and unions Φ 1 "Calculation per 1 pc. Really built on the property. | pcs | 10 | 0
18 | Supply and installation of sprinkler Φ1"Calculation per 1 pc. Really built on the property. | pcs | 116 | 0
19 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 254.52 | 0
Calculation per m of finished work.
TOTAL 3.3. ASSEMBLY WORK
TOTAL 3. SPRINKLER NETWORK
REKAPITULATION
1. PLUMBING
2. SEWAGE
3. SPRINKLER NETWORK
Total:
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit like types: KNND d50 12/9-FM, FTT, RPDTA, KDTA, L, VF***12/9-A, FTT, RPDTA, L,VF (9750 m3/h) product of «Hidria» Slovenia completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 60C /59% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 9750 m3 / h, the external pressure drop 500 Pa
-Flexible connection
-Air axhaust:
-Flexible connection
-Suction-section of vertical air intake
-Section-filtration fabric filter class F5
-Section-plate recuperator effectiveness min. 60% in summer
-Section-fan with direct drive in protiveksplozivnoj EX version, vertical discharge, flow of 9750 m3 / h, the external pressure drop 500 Pa
-Blinds- waste air
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 70 kW at evaporating temperature and the outside temperature 50C to 460C
- 35kW heating capacity at outside temperature70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
|  | set | 1 | 0
4 | Roof radial fan in the anti-explosive performance, Klima Celje, Slovenia. Type EX AVS 450-4T- AP, N=0,9/0,6 kW.
Some of the equipment cooling fan are:
- Flexible connector
- Auto -lift shutters
- Flange
- Supporting structure for the pitched roof in thermal protection
- Frequency regulator for speed control
|  | set | 1 | 0
5 | Roof radial fan,Klima Celje, Slovenia. Type EX SVK2-400/315-4/6,N=0,66/0,45 kW . Some of the equipment cooling fan are:
- Flexible connector
- Auto -lift shutters
- Flange
- Supporting structure for the pitched roof in thermal protection
- Frequency regulator for speed control
|  | set | 1 | 0
6 | Equipment for air distribution like of the Hydra in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
- Exterior steel grate with additional protection when working in touch with Saharan sand
Type APZR/ANŽ-4/3 size 1250x850
- exterior exhaust grid of stainless steel type AZR/ANŽ-4/3 size 1200x800
- Diffuser for air supply with a box, model OD-11V/S/I19/Ex in a panel 600x600 mm
Size 160
| Size 200 | pcs | 1 | 0
Size 250
| Size 315 | pcs | 1 | 0
Air flow regulator MRP-1/Ex iin front of OD-11/V
Size 125
| 160 | pcs | 2 | 0
| 200 | pcs | 6 | 0
| 250 | pcs | 8 | 0
| - Exhaust grid with flow regulator | pcs | 6 | 0
Size 350x250
300x200
| 450x450 | pcs | 2 | 0
| - Fire damper wall width L= | pcs | 6 | 0
| PL-15 EL120S/A2/T12/Ex-Z | pcs | 8 | 0
| Size 250x250 | pcs | 6 | 0
400x250
| 400x300 | pcs | 1 | 0
| 400x400 | pcs | 1 | 0
| 500x400 | pcs | 2 | 0
Pillar boxes for the removal of air from the space type LN-3 from two strainers with filter F5 and manual control flow made ​​of stainless steel
| -height h = 3000, port f 250 | pcs | 2 | 0
| - pillar according to inox detail, of stainless steel height = 3000 from pipes f 160 with two translucent valves PV 1/160 | pcs | 2 | 0
|  | pcs | 2 | 0
|  | pcs | 8 | 0
|  | pcs | 4 | 0
|  | pcs | 12 | 0
|  | pcs | 5 | 0
7 | Galvanized sheet metal ducts of square and circular diameter of plate 0.8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 1600 | 0
8 | Aluminum flexible tube in dropped ceilings with mineral wool insulation of 25 mm and an outer sleeve of aluminum foil
f 160
f 200
| f 250 | m | 25 | 0
|  | m | 25 | 0
|  | m | 50 | 0
9 | Ventilation of sanitary facilities from
-ranslucent valve PV 100 (kom.4),
-PE pipe f 160 (10 m)
-radial duct fan CA 150, N=85 W
-supplies for making
| Set | set | 1 | 0
10 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 140 | 0
11 | Fine regulation, commissioning, testing capacity and quantity. | commissioning | 1 | 0
12 | Split air conditioners for cooling performance, product of LG Electronic with power of 2.5 kW. (incorporated in the oversight room No.20)
|  | pcs | 1 | 0
| Total air conditioning equipment: |  |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_23"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks GRO.B_23. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
TOTAL :
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| 2x XP00-A ( 4x240 + 120 mm2) (GRO -DO-TS) | m | 100 | 0
| NHXH E60 4x35mm2 | m | 55 | 0
| PPOO 3x25+16 mm2 | m | 15 | 0
| PPOO-Y 5x16 mm2 | m | 110 | 0
| PPOO-Y 5x10 mm2 | m | 10 | 0
| PPOO 4x6 mm2 | m | 110 | 0
| PPOO 4x4 mm2 | m | 190 | 0
| PPOO-Y 5x2,5 mm2 | m | 320 | 0
| PPOO-Y 4x2,5 mm2 | m | 430 | 0
| PPOO-Y 5x1,5 mm2 | m | 196 | 0
| PPOO-Y 3x2,5 mm2 | m | 180 | 0
| PPOO-Y 1x50 mm2 | m | 30 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 320 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 20 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
TOTAL II :
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 50 | 0
| PNK 200 | m | 250 | 0
| PNK 300 | m | 360 | 0
| Slat cable carriers 200 mm | m | 250 | 0
| Slat cable carriers 300 mm | m | 360 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 40 | 0
3 | Other small material | flat | 1 | 0
TOTAL III:
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 24 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 78 | 0
3. | The floodlight is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air.Hazardous zones: 1,2, 21, 22. Housing: aluminium powder painted casting Diffuser: borosilicate tube glass, IP 66 in accordance with EN 60529+A1, category 1, RLF/500 QT, 500 W,E40 Accessories: protected galvanized steel gird, assembly kit for wall, pipe and ceiling mounting II 2GD Ex de IIC T3/T4 or Ex d IIC T4-T3 tD A21 IP66 T10ºC-150ºC, 231V, 60 Hz, TEP,ZAGREB , Croatia | piece | 6 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 6 | 0
5. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 8 | 0
6. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 14 | 0
7. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 9 | 0
8. | Other unspecified material needed for the installation | kpl | 1 | 0
9. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
TOTAL IV :
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 130 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 17 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 100 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 96 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 5 | 0
| .serial water-proof n/ž | piece | 8 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 4 | 0
| SKX 12/22 Serial switch SMS 03/8 - switch actuator SMO 17/5 - cable gland SPU 25, Type: SKX 12/22, TEP | piece | 8 | 0
| SKX 12/32, Pushbutton PBT 01 -pushbutton actuator SPO 01/1 - cable gland SPU 25, TEP | piece | 3 | 0
| SKX 13/11 Pushbutton PBT 01 - SPO 01/1 - Signal lamp SLP - Front element of signal lamp SPO 02/2 - cable gland SPU 25 | piece | 2 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 1P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 9 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 2 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 1P+E, enclosure shall begray, Type GHG 511 440 SR 0001, TEP | piece | 1 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL V.1 :
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 100 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 20 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 30 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 100 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 5 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL VI:
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 3 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 35 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 3 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 11 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 13 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
TOTAL VII:
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 9 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 220 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 9 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm | piece | 9 | 0
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 9 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 220 | 0
| -PP00-Y 3x2,5 mm2 | m. | 60 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 230 | 0
| - PVC warning tape | met | 230 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
TOTAL VIII KM:
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
TOTAL IX:
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 9 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 9 | 0
3. | Protective canopy drip-channel for detector. | piece | 9 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 2 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 18 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 12 | 0
7. | Marking elements with persistent marks | piece | 9 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
TOTAL FLAME DETECTORS :
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 8 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
| Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 5 | 0
3 | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 3 | 0
4 | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 11 | 0
5 | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 4 | 0
6 | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 3 | 0
7. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 4 | 0
8. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
9. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 39 | 0
10. | Supply and delivery of mark elements for the fire alarm system | piece | 22 | 0
11. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
12. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
13. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
14. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
15. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
16. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
17. | Other unspecified fine material. | kpl. | 1 | 0
18. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0
TOTAL MANUAL TRANSMITTER
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain | piece | 1 | 0
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 2 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 2 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 3 | 0
6. | Marking elements with persistant marks | piece | 3 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
TOTAL SIRENS :
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 4 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 2 | 0
5. | Marking elements with persistant marks | piece | 2 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
TOTAL FLASHES:
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 2 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
· 1 piece of the Power supply unit 24V, 5A,
· 1 piece of the rechargeable battery 2x12V, 7,2Ah,
· 1 piece of the automatic fuse 6A,
· relay vard with three relays 24V/2A
· 40 pieces of Two-stairs VS terminals 1.5mm2,
· spaces for safety barriers
· spaces for MDI module
· spaces for SOM module
· 1 piece of the. DIN šina,
· perforated tiles with lid
· other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
Creating attests authorized by the domestic industry.
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 1 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 1 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 25 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box | m | 250 | 0
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 120 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 120 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 190 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 180 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 30 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 20 | 0
8. | Delivery and installation cable P/F 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 100 | 0
9. | Other unspecified fine material. | m. | 15 | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
TOTAL COMMISSIONING :
TOTAL IX
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 280 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 14 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 30 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 20 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 8 | 0
| Measuring tape-wire connectors: |  | 14 | 0
| KON 02, Rf 40 122 | pieces | 12 | 0
Drip:
| KON 21; Rf 200212 | pieces | 22 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 12 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 16 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 14 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 14 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 11 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 240 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 320 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 44 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 140 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
TOTAL X :
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS
II) | POWER CABLES
III) | CABLE CARRIERS AND INSTALLATION PIPES
IV) | FLASHLIGHTS
V) | ILIGHTNING INSTALLATION
VI) | OUTLET AND FEEDER INSTALLATIONS
VII) | POTENTIAL EQUALIZING INSTALLATIONS
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE
IX) | FIRE DETECTION SYSTEM
X) | LIGHTNING ROD INSTALLATION
XI) | TESTING AND MESAURING
XII) | PROJECT OF CREATED STATE
| TOTAL |  |  | 0
0

## B-24 MECH
3. BILL OF QUANTITY-HYDRO (B-24)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
1.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 5.61 | 0
Calculation per m3 of finished work. (2x0,90x0,6+1.2x12.x12)x2. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.48 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 6.16 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS
1.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
TOTAL 1.2. MASONRY AND BRICKLAYERING WORK
1.3. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 2" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 11.02 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 5.56 | 0
Calculation per m of finished work
6 | Supply and installation of flat leaky ball valve Φ 2" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 1 | 0
Calculation per 1 pc. really built on the property.
7 | Supply and installation of flat leaky ball valve Φ 1" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 4 | 0
Calculation per 1 pc. really built on the property.
9 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 16.58 | 0
Calculation per m1 finished work.
TOTAL 1.3. ASSEMBLY WORK
TOTAL PLUMBING
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling unit like types: KNND d50 6/6-FM, FTT, RPDTA, KD, BD, L, VF***6/6-A, FTT, RPDTA, L, VF, (2150 m3/h) proizvod «Hidria» SloveniA completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 220C
-Winter-design conditions:
Outdoor air: 100C /59% r.v., space 220C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 2150 m3 / h, the external pressure drop 500 Pa
-Flexible connection
Drain part:
-Flexible connection
Suction-section of vertical air intake
Section-filtration fabric filter class F5
Section-plate recuperator effectiveness min. 60% in summer
Section-fan with direct drive in protivekspolzivnoj EX version, vertical discharge, flow of 2150 m3 / h, the external pressure drop 500 Pa
Louvre-waste air
-Flexible connection
|  | set | 1 | 0
2 | Compressor condensing units as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 22 kW at evaporating temperature and the outside temperature 50C to 460C
- 20kW heating capacity at outside temperature 7 0C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
|  | set | 1 | 0
4 | Equipment for the distribution of air as in Hidria anti-explosive Product Placement Ex zone 1 and accompanying attest documentation
- Suction external-steel grate with additional protection for work in contact with sand type APZR/ANŽ-4/3, smoke. 650x550
-exhaust exterior steel grate
AZR/ANŽ-4/3 type of smoke. 650x550
-diffuser for air supply with a box model
| OD-11V/Ex, size 250 | pcs | 1 | 0
-fireproof-damper wall width L = 450
| PL-15 EL120S/A2/T12/Ex-Z | pcs | 1 | 0
dim.500x250
| -Pole-diffuser made ​​of stainless steel for the removal of air from the space | pcs | 4 | 0
SD-2/800 type, H = 800
-Flow regulator for air MRP-1/Ex stubnog front diffuser, size f 250
|  | pcs | 2 | 0
|  | pcs | 2 | 0
|  | pcs | 2 | 0
5 | Galvanized sheet metal ducts of square and circular diameter of plate 0.8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg | 400 | 0
6 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 65 | 0
7 | Fine regulation, commissioning, testing capacity and quantity.
|  | commissioning | 1 | 0
Total equipment for air conditioning:
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS |  |  |  | 0
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "RO.B_24"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_24. (See related scheme 103.1.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
TOTAL :
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00-A 4x50 mm2 (RO -DO-TS) | m | 100 | 0
| NHXH E60 4x35mm2 | m | 30 | 0
| PPOO 4x16mm2 | m | 15 | 0
| PPOO-Y 5x10 mm2 | m | 13 | 0
| PPOO-Y 5x4 mm2 | m | 14 | 0
| PPOO-Y 5x2,5 mm2 | m | 5 | 0
| PPOO-Y 5x1,5 mm2 | m | 20 | 0
| PPOO-Y 3x2,5 mm2 | m | 5 | 0
| PPOO-Y 1x35 mm2 | m | 30 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 20 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 4 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
TOTAL II :
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 10 | 0
| PNK 200 | m | 25 | 0
| Slat cable carriers 200 mm | m | 25 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 10 | 0
3 | Other small material | flat | 1 | 0
TOTAL III:
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 8 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 2 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 1 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 1 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 1 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 1 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
TOTAL IV :
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 9 meters. | piece | 10 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 2 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 15 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 33 | 0
5.5. | procurement and installation switches installation
| .simple water-proof n/ž | piece | 1 | 0
| .serial water-proof n/ž | piece | 1 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 1 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL V.1 :
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 10 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 5 | 0
3. | Delivery and installation of PVC two part channel dimensions 65x150 mm complete with lid, final elements and couplings. The same type as DLP, Legrand or equivalent | met | 5 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 35 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 4 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 3 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 4 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL VI:
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 3 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 4 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 8 | 0
6 | Creating bypass Gauge | piece | 1 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
TOTAL VII:
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 3 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 70 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 4 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 1 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 35 | 0
| -PP00-Y 3x2,5 mm2 | m. | 6 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 40 | 0
| - PVC warning tape | met | 40 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
TOTAL VIII KM:
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 1 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
TOTAL IX:
X) | SYSTEM FOR FIRE DETECTION
FLAME DETECTORS
1. | Flame Detector with triple detector of infrared radiation in order to eliminate false alarms IR3 (Eex "d"), type 40/40 SharpEye Spectrex or equivalent, in the aluminum enclosure, IP 66/67, ATEX Eexd.Triple Sensor high speed response time, 150 msec, programmable configurations, immune to false alarms (resistant to sunlight ..) standard 4-wire connection, FM, CSA, ATEX, IECEx , EN 5410, FM 3260 attested, Eexde Version | piece | 2 | 0
2. | Pan-tilt carrier for detector SharoEye 40/40. | piece | 2 | 0
3. | Protective canopy drip-channel for detector. | piece | 2 | 0
4. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm type MDI 82 Securiton Switzerland or similar. The module should have VdS approval. | piece | 1 | 0
5. | Cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
6. | Plugs for cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
7. | Marking elements with persistent marks | piece | 2 | 0
Other unspecified fine material.
8. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
TOTAL FLAME DETECTORS :
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 2 | 0
2 | Hand conventional fire detector in blue color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC V Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the +50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. | piece | 1 | 0
3. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 1 | 0
4. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0
5. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0
6. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 2 | 0
7. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0
8. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
9. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
10. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 7 | 0
11. | Supply and delivery of mark elements for the fire alarm system | piece | 5 | 0
12. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
13. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
14. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
15. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
16. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 2 | 0
17. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
18. | Other unspecified fine material. | kpl. | 1 | 0
19. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0
TOTAL MANUAL TRANSMITTER
9.3. | FLASH AND SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain |  |  | 0
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 1 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 1 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 1 | 0
6. | Marking elements with persistant marks | piece | 2 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 1 | 0
TOTAL SIRENS :
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 1 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 1 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 1 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 1 | 0
5. | Marking elements with persistant marks | piece | 1 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 1 | 0
TOTAL FLASHES:
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
Creating attests authorized by the domestic industry.
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 3 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 3 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 4 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box |  |  | 0
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 15 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 12 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 12 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 10 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 10 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 25 | 0
9. | Other unspecified fine material. | m. | 15 | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
TOTAL COMMISSIONING :
TOTAL IX
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 50 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 2 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 2 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 4 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 3 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 2 | 0
Drip:
| KON 21; Rf 200212 | pieces | 2 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 2 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 1 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 10 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 6 | 0
Catching bats:
Catching bat H= 13 m (circumferential parapet-complete with struts):
| LOP 13 ; Rf 300513 | pieces | 6 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 30 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 190 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 10 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 26 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
TOTAL X :
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS
II) | POWER CABLES
III) | CABLE CARRIERS AND INSTALLATION PIPES
IV) | FLASHLIGHTS
V) | ILIGHTNING INSTALLATION
VI) | OUTLET AND FEEDER INSTALLATIONS
VII) | POTENTIAL EQUALIZING INSTALLATIONS
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE
IX) | FIRE DETECTION SYSTEM
X) | LIGHTNING ROD INSTALLATION
XI) | TESTING AND MESAURING
XII) | PROJECT OF CREATED STATE
| TOTAL |  |  | 0
0

## B-25 MECH
3. BILL OF QUANTITY-HYDRO (B-25)
SERIAL NUMBER | SERIAL NUMBER | Unit of measure | Quantity | Total price
1. PLUMBING
1.1. EARTHWORKS
1 | Manual excavation of a trench (width 80cm) in materials of III and IV categories, along with loading and transport of excavated material and the bottom of the channel planning. | m3 | 2.8 | 0
Calculation per m3 of finished work (2x0,90x0,6+1.2x12.x12)x2. =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3of finished work. (2x0,60x0,2)x2 =
3 | Backfill of the trench with the excavation material in layers 30 cm thick along with proper compaction. | m1 | 3.08 | 0
Calculation per m3of finished work. ((2,81-0,24) x 1,2)x2 =
TOTAL 1.1. EARTHWORKS
1.2. CONCRETE WORKS
1 | Making the connecting shafts of concrete, MB 20 in the corresponding panel. The size and shape of the detail. To carry out treatment on walls and install creepers. | m3 | 1.1 | 0
1,2x1,2x0,35x1 + 0,8x0,75x1 =
1.2. TOTAL CONCRETE WORKS
1.3. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
3 | Supply and installation of cover 80x80 and transport capacity 25 tones | pcs | 1 | 0
TOTAL 1.3. MASONRY AND BRICKLAYERING WORK
1.4. ASSEMBLY WORK
1 | Supply and installation of steel galvanized water pipes Φ 3" (DN80mm), with the connections, cold water according to the plans of the project, together with associated fittings. | m1 | 8.42 | 0
Calculation per m of finished work
2 | Supply and installation of steel galvanized water pipes Φ 2" (DN50mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 5.04 | 0
Calculation per m of finished work
3 | Supply and installation of steel galvanized water pipes Φ 1" (DN25mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 45.83 | 0
Calculation per m of finished work
4 | Supply and installation of steel galvanized water pipes Φ 3/4" (DN20mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 15.65 | 0
Calculation per m of finished work
5 | Supply and installation of steel galvanized water pipes Φ 1/2" (DN15mm), with the connections, cold water according to the plans of the project, together with associated fittings. Assembly for washing objects. | m1 | 41.65 | 0
Calculation per m of finished work
6 | Supply and installation of flat leaky ball valve Φ 1" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc. | 4 | 0
Calculation per 1 pc. really built on the property.
7 | Supply and installation of flat leaky ball valve Φ 1/2" on each trace distribution of cold water and test functioning. Valves are supplied with a chrome handle for opening and decorative chrome bezel. | psc | 33 | 0
Calculation per 1 pc. really built on the property.
8 | Testing by placing plumbing network under test pressure of 10 bar. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bar. | m1 | 116.55 | 0
Calculation per m1 finished work.
TOTAL 1.4. ASSEMBLY WORK
1.5. SANITARY DEVICES NAD SANITARY ACCESSORIES
SANITARY APPLIANCES AND ACCESSORIES
NOTE:
Type and color of the sanitary equipment contractor should offer, in agreement with an investor or an architect, and then contracting and total access and installation of the same order. Sanitary ware and fittings must be first-class (white), with chrome and feeders, like the type GEBERIT, GROHE, DOLOMITE, LAUFEN or equivalent. Ports-microclimate of supply and sanitary sewers run after approval by investors.
1, | toilet bowl | pcs | 2 | 0
Supply and installation of toilet bowl faience class (sanitary ware), white color, fully functional version with full cover with plastic and planks, cistern (low installated) with angle valve and drain in the floor. Calculation per piece complete installed toilet bowl.
2 | Washbasin | pcs | 4 | 0
Supply, transmission and assembly of faience washbasins class, approx 55 cm, together with chrome trap and connecting material mixer for hot and cold water, and angle valve Ø 1/2 "and all connecting material.
Calculation per piece complete built sinks.
3 | Sink | pcs | 1 | 0
Supply, transmission and mounting the sink class, approx 120x60 cm, together with chrome trap and connecting material mixer for hot and cold water and all connecting material.
Calculation per piece complete built sink.
4 | Sanitary accessories
Supply and installation of sanitary accessories (class I - INOX, or Kimberly-Clark or equivalent) with toilets:
| a) articles for cleaning toilets |  | 2 | 0
| b) toilet paper holder |  | 2 | 0
| c) Wall mirror dimensions 600x400 mm, thickness of 4 mm, with polished edges |  | 4 | 0
| d) paper towels holder |  | 4 | 0
| e) container for liquid soap |  | 4 | 0
TOTAL:
TOTAL 1.5 SANITARY DEVICES NAD SANITARY ACCESSORIES
TOTAL 1. WATER SUPPLY
2. HYDRANT NETWORK
2.1. EARTHWORKS
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3 | 0 | 0
Calculation per m3 of finished work.
-----x0,90x0,6
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0 | 0
Calculation per m3 of finished work.
------x0,60x0,2
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1 | 0 | 0
Calculation per m3 of finished work.
| ( 1 - 2 ) x 1,2 |  |  | 0
TOTAL 2,1. EARTHWORKS
2.2. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Installation of wall penetration without protective pipe DN 80 and DN 100 for "dry mounting" in but left holes in slabs and walls for plumbing penetrations along with repeated closing holes in all the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | Psc
TOTAL 2.2. MASONRY AND BRICKLAYERING WORK |  |  |  | 0
2.3. ASSEMBLY WORK
1 | Supply and installation of galvanized water pipes with necessary fittings, for cold and hot water according to the plans of the project, together with associated fittings.
Calculation per m of finished work.
| Φ 2" (DN50mm), | m | 20.07 | 0
| Φ 3" (DN80mm), | m | 32.62 | 0
2 | Supply and installation of a fire hydrant F50 mm for extinguishing Class A for materials and incorporating the entire hydrant two parts standing cabinets of stainless steel sheet, the project dimensions: width 500mm, depth 150mm and height of 1200mm. The hydrant complete includes: union brass faucet F50 mm, pressure hose - Trevira rubber length 20 m and the brass hose end. | pcs | 4 | 0
Calculation per piece.
3 | Procurement and installation of equipment for extinguishing fires of class A, B, C, D and E (all fires) powder, S-9, 9 kg JUS.Z.C2.035 content. It is anticipated that the unit is installed in each hydrant cabinet. The operation time is 22 sec jets, jets range 3 - 4 m, and the temperature range of-20oC to +60 OC. | Pcs. | 40 | 0
Calculation per piece.
4 | Testing plumbing putting the network under test pressure of 15 bars. The installation has to be under pressure as long as it does not inspect all connections. Minimum duration of the probe can be 120 minutes. Pressure drop must not exceed 0.1 bars. | m1 | 52.69 | 0
Calculation per m1 finished work.
3 | Flushing water mains. | pcs
Calculation per m1 finished work.
TOTAL 2.3. ASSEMBLY WORK
TOTAL 2. HYDRANT NETWORK
3. SEWAGE
3.1. | EARTHWORKS
1 | Manual excavation of a 80cm wide trench in materials of categories III and IV, along with loading and transport of excavated material and planning of the bottom of the channel. | m3 | 2.8 | 0
Calculation per m3 of finished work.
2x0,90x0,6+1.2x12.x12) =
2 | Development of the placenta from the sand, along with planning and compaction. | m3 | 0.24 | 0
Calculation per m3 of finished work.
(2x0,60x0,2) =
3 | Backfill of the trench with excavation material in 30 cm thick layers along with proper compaction. | m1 | 3.08 | 0
Calculation per m3 of finished work.
(2,81-0,24) x 1,2) =
TOTAL 3.1 EARTHWORKS
3.2 | CONCRETE WORKS
1 | Making revision shafts of concrete, MB 20 in the corresponding panel. The size and shape of the detail. To carry out treatment on walls and install creepers and cover. |  | 1.1 | 0
m3
TOTAL CONCRETE WORKS
3.3. MASONRY AND BRICKLAYERING WORK
Holes for fitting the plumbing installations will be left during construction of AB structures. In the event of a change there will be a hand-made hole.
1 | Consuming breaking of openings in slabs and walls for plumbing penetrations along with repeated closing holes in all according to the technical requirements and technical regulations for this type of work. |  | 0 | 0
| Calculation per piece. | pcs
2 | Slice consuming breaking in slabs and walls for laying water pipes along with slice reclosing according to all the technical requirements and technical regulations for this type of work. | m1 | 0 | 0
Calculation per piece.
3 | Supply of sewage vertical in height of 306 cm from upper quote of roof. Size 25x25 cm | pcs | 1 | 0
4 | Supply and installation of cover 80x80 and transport capacity 25 tones | pcs | 1 | 0
TOITAL 3.2. ASONRY AND BRICKLAYERING WORK
Supply of materials, transport, mounting, thermal isolation, functional and pressure testing
1 | PVC sewer pipe for home sewers
Supply and installation of PVC sewer pipe for the performance of internal sewage system, according to DIN 8061 and DIN 19531, with all necessary wiring and fittings and small installation material. Sealing sewer pipes exported rubber rings. Bid to define the exact type offered sewer, pipes with a certificate that guarantees the quality of pipes and fittings attached. Mandatory sample and approval before making the installation and approved by supervision, enrollment in the construction diary. Pipes of dubious quality, without adequate documentation attests forbidden installed. Mandatory photo documentation as built before backfilling the trench in paragraph 1.1.).
The item was included in the work and all materials, pipe fittings, auxiliary material for joining and fixing - clips for fixed and sliding points.
Calculation per m built sewers.
| DN 200 | m | 10.11 | 0
| DN 110 | m | 91.74 | 0
| DN 50 | m | 58.9 | 0
2 | PVC sewer revision / sweepers | pcs | 6 | 0
Supply and installation of PVC sewer audit / sweepers for installation in the bottom of the control shaft AB.
Calculation per piece embedded audit / sweepers.
DN 110
3 | Floor drain
Supply and installation of floor drains or similar type HL310NPrR with round stainless plate, grille and side with the float to stop gases in case the drain without water.
Calculation per piece.
| Ø 110 | pcs | 4 | 0
| Ø 50 | pcs | 1 | 0
4 | PVC ventilation cap | pcs | 6 | 0
Supply and installation of vertical sewer vent caps, along with copper flashings complete with a link to waterproof (as type Braas or equivalent). Ventilation cap (set) Ø 50 mm.
Calculation per piece fitted caps.
5 | Testing sewage facility | m | 160.741 | 0
Testing of complete sewage facility with associated buildings pane and header tanks, etc.) on the bandwidth and functionality. Testing performed prior to closing pipeline trenches and painting with photographic documentation of the required item 1.1 .. After successful completion of testing the functionality and impermeability, about the same issue a certificate. In paragraph including developing rules / instructions on the operation and maintenance of the entire drainage
system object.
Calculation per m 'tested networks.
TOTAL 3.4. ASSEMBLY WORK
TOTAL 3. SEWAGE
3.4 ASSEMBLY WORK
RECAPITULATION
1. PLUMBING
2.SPRINKLER NETWORK
3.SEWAGE
4. PRECIPITATOR
Total:
Machinery documentation(B-06)
No | An item of bill of quantities - equipment for air conditioning - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Air handling type KNND d50 12/9-FM, FTT, RPDTA, KDTA, L, VF***12/9-A, FTT, RPDTA, L, VF (8700 m3/h) from Slovenia Hidria completely made of:
-Housings-painted inside and out in RAL 7035, class of thermal transmittance T2 class TB2 thermal bridges, the mechanical stability of D1.
-Summer-design conditions:
Outdoor air: 440C / 6% r.v., space 210C
-Winter-design conditions:
Outdoor air: 60C /80% r.v., space 210C
-Feeder supply part:
-Flexible connection
-Air intake
-Section-filter with metal filter class G3 filtration
-Section with a bag filter class F7 filtration
- Section of plate recuperator with efficiency min 60% in summer period
-Section DX-reversible heat exchanger, outlet temperature of 150C in summer
-Empty sections
-Section-fan, direct drive, vertical discharge, flow of 8700 m3/h, the external pressure drop 500 Pa
-Flexible connection
Drain part:
-Flexible connection
Suction-section of vertical air intake
Section-filtration fabric filter class F5
- section of plate recuperator efficiency min. 60% in summer period
-Section of ventilator with direct drive, vertical discharge in »Ex« execution, flow with two values 8700 m3/h, external pressure drop 500 Pa
-Flexible connector
|  | set | 2 | 0
2 | Compressor condensing units for offices part as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 60kW at evaporating temperature 5° and the outside temperature 460C
- 25 kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
3 | Compressor condensing units for laboratory part as of Hidria for outdoor installation in the performance of reversible heat pumps
- A tropical version for operation up to 520C
- Freon R410A
- The unit is equipped with its own automatic control of the cooling process, the ability to connect to BMS
- Cooling capacity of 55kW at evaporating temperature 5° and the outside temperature 460C
- 25 kW heating capacity at outside temperature 70C
The price includes connection of compressor condensing unit with air chamber.
|  | set | 1 | 0
4 | Control equipment includes air chambers
- DDC controller
- Electrical cabinets (condensing unit power over cabinet air chamber)
- Pressure sensors
- Sensors dirty filter
- electric motor drives of dampers with spring return
-elements of automation within the air chambers in the explosion-proof design
|  | set | 2 | 0
5 | Equipment for air distribution like of the Hidra Sl.in the anti-explosive performance of space Ex zone 1 and accompanying documentation attesting in all of the Hidria like:
-Exterior steel grate with additional protection when working in touch with Saharan sand
type APZR/ANŽ-4/3 size 1250x850
- exhaust exterior steel grate
Type AZR/ANŽ-4/3 size 1250x850
- Outer protective grid with protective stainless steel mesh
| AZR-3/2,size.400x800 | Pcs | 2 | 0
- Line diffuser for air supply and exhaust of air with flow regulation
| LD 13/4,L=2000 mm | Pcs | 2 | 0
LD 13/4,L=1000 mm
| - suction and discharge grid as AR 17 with flow regulation | Pcs | 6 | 0
Size 525x325
| Size 425x425 | Pcs
Size 325x325
| -Grid on the laboratory doors AR-4P | Pcs | 66 | 0
| Size 425x425 | Pcs | 11 | 0
|  | Pcs | 5 | 0
|  | Pcs | 1 | 0
|  | Pcs | 3 | 0
|  | Pcs | 11 | 0
6 | Galvanized sheet metal ducts 0,8 mm with sealing, making of connections, accessories for hanging, openings for cleaning and everything else that is necessary for the completeness of creating installation including testing and balancing.
|  | kg. | 4200 | 0
7 | Aluminum flexible pipes with insulation of mineral wool 25mm and outer sheath made from aluminum foil f 200
|  | m | 200 | 0
8 | Insulation sheet metal channels with self-adhesive foam mass (λ = 0.04 W / mK) which in itself has affixed aluminum foil 25 mm thick reinforced with the channel strips and edge profiles.
Calculated per m2
|  | m2 | 620 | 0
9 | Fine regulation, commissioning, testing capacity and quantity. | commissioning
|  |  | 1 | 0
Total air conditioning equipment:
3.2. Equpiment for LPG
No | An item of bill of quantities - equipment for LPG - delivery, transportation, assembly- | Unit of measure | Quantity | Total price
1 | Bottles for LPG from 25 kg with valve R ½” | pcs | 6 | 0
2 | -Distributors for LPG off 5/4” for six bottles and sif connectors R ½”
| -Connecting flexible hose from bottle to distributor | pcs | 1 | 0
f ½”, L=1,0 m for NP25
| -Valve for LPG on distributor R ½”, NP25 | pcs pcs | 6 | 0
|  |  | 6 | 0
3 | Reductive valve for reduction LPG from liguid to the gas phase
R 5/4” from 18 bars to 1,0 bar
| R 5/4” from 1 bars to 30-50 mbars | pcs pcs | 1 | 0
| Safety valve R ½”,opening at 18,3 bar | pcs. | 1 | 0
| Manometer 0-25 bars with valve in front of |  | 1 | 0
| R ½” NP25 | pcs
| Manometer 0-100 mbars with valve in front of | pcs | 1 | 0
R ½” NP25
|  |  | 1 | 0
4 | Outer protective grid with protective mesh made of stainless steel as Hidria Slovenia
AZR-3/2,size 800x1000
|  | pcs | 2 | 0
5 | Steel pipes with auxiliary and consumables material painted yellow
f 21,3 x 2 (1/2”)
| f 26,9 x 2,3 (3/4”) | m | 54 | 0
| f 33,7 x 2,6 (1”) | m | 18 | 0
| f 42,45x2,6 (5/4") | m | 24 | 0
|  | m | 24 | 0
6 | Reinforcement bars at the the gas installation LPG
In design NP 25
| R ½” | pcs pcs | 30 | 0
| R 3/4” | pcs | 3 | 0
| R 5/4” |  | 1 | 0
7 | General costs, testing and commissioning | arbitrary | 1 | 0
TOTAL Equipment for LPG: |  |  |  | 0
CONSUMPTION LIST OF ELECTRICAL INSTALLATIONS
A) | HIGH CURRENT
In all of the following items, with respect and specific description of the item, it is involved following: purchase, delivery to site and installation of specified materials, including all the necessary technological operations, all the necessary chores mounting material, furthermore all the necessary electrical connections to the full functionality including all necessary chores connecting material and all associated preparatory or finishing work including cleaning and removal of excess and residual materials, etc.
2. | THE QUOTE FOR WORKS- ELECTRICAL AND LIGHTNING ROD INSTALLATIONS
ORDINAL | ACTIVITY DESCRIPTION | MEASURE UNIT | QUANTITY
TOTAL
I) | DISTRIBUTION CABINETS
Note: Possible producers of equipment for the distribution cabinets are: Schneider Electric, Siemens, ABB.
1.1. | DISTRIBUTION CABINET "GRO.B_25"
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_25. (See related scheme 1.4.!) Following equipment have to be installed in main distribution cabinet:
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_25.1 (See related scheme 1.5.!) Following equipment have to be installed in main distribution cabinet:
Supply and installation of the free-standing distribution cabinet made ​​of two times pickled sheet metal painted with fundamental and final paint using electrostatic treatment and with the project marks RO.B_25.2 (See related scheme 1.6.!) Following equipment have to be installed in main distribution cabinet:
Note: It should be worked on this DISTRIBUTION after definition of technological consumers with addition of protection elements for all consumers in the building!
| All together | piece | 1 | 0
TOTAL :
II) | POWER CABLES
1 | Supply and installation of power cables for distribution. Cables are installed in cable carriers or ground trench and prepared the following types and sections:
| XP00- 4x95 mm2 (GRO -DO-TS) | m | 100 | 0
| PPOO 4x25 mm2 | m | 15 | 0
| PPOO 4x16mm2 | m | 70 | 0
| NHXH E60 4x6mm2 | m | 15 | 0
| PPOO-Y 5x4 mm2 | m | 10 | 0
| PPOO-Y 5x2,5 mm2 | m | 50 | 0
| PPOO-Y 5x1,5 mm2 | m | 250 | 0
| PPOO-Y 3x2,5 mm2 | m | 680 | 0
| PPOO-Y 1x16 mm2 | m | 70 | 0
2 | Cable with copper conductors, insulation of cross-linked polyethylene (XLPE), filling of hardened rubber, designed for high mechanical and electrical loads, "reduced flammability" and emissions of hazardous gases, type or similar.
| VO-YMvKmbas 5/4/ 3x1.5 mm2 | m | 50 | 0
3 | Sealing cables crossing between fire fireproof sector mass | kg | 5 | 0
4 | Other small materials (lugs, clamps, ...) | flat rate | 1 | 0
5 | Testing performed installation with commissioning (putting into operation mode) | flat rate | 1 | 0
TOTAL II :
III) | AN INSTALLATION CABLE CARRIERS AND TUBES
Supply and installation of galvanized cable mounting cable strong and weak currents. The price includes the complete accessories and supplies for installation and connection cable bracket (brackets, clamps, bolts). Cable carriers are the following dimensions and types:
1 | Perforated cable racks for medium loads with blade 300x50x1 mm for external assembly (hot dip galvanizing zinc) and complete installation material (clamps, brackets)
| PNK 100 | m | 40 | 0
| PNK 200 | m | 70 | 0
| Slat cable carriers 200 mm | m | 70 | 0
2 | Supply and installation of protective metal hoses of various dimensions (1 ", 2", 3 ") to protect the cables out of cable channels or cable tray, types and dimensions
| PVC pipe with diameter 100 mm | m | 10 | 0
3 | Other small material | flat | 1 | 0
TOTAL III:
IV) | LIGHTERS
Note: The price must include lamps and related lamp!
1 | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2, 21, 22. Ex fluorescent light fitting type FLX is used as fluorescent lighting fitting with two TC- TSE fluorescent compact lamps 36W with 2G11 lampholder., Ex de IIC T5/T6, Ex d IIC T5/T6 tD A21 T90°C/T80°C, 231V, 60 Hz, | piece | 10 | 0
2 | Monsun®, damp-proof luminaire, primary light control with reflector, of sheet steel, white, primary optical cover: enclosure, of PMMA, inner prismatic structure, light emission: direct distribution, primary light characteristic: symmetric, installation type: suspended mounting, surface-mounted, for 2 x T26 36W, ballast: ECG, with terminal, 3-pole, max. 2.5mm², mains connection: 230V, AC, 60Hz, luminaire housing, of glass-fibre reinforced polyester.Siteco | piece | 8 | 0
| Comfit Plus , Individual luminaire recessed mounted, Steel hosing, luminaire white finished BAP60/Cat.2 louvre , Degree of protection: IP 23, Protection class: I, Mouting type: recessed Modul 625 Tip 5LP 11474A 4x18W, Siteco | piece | 166 | 0
3. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Hazardous zones: 1,2. The luminaire is also destined to be used in mine industry.Ex ed I/IIC T2/T3, on request, II 2G Ex ed IIC T2,T3 230 V, AC, 60Hz ,60W max. DIN 49810 Bl.4, Type 0403.24/10, TEP Croatia | piece | 1 | 0
4. | The luminaire is designed to light the industrial areas and facilities, also outdoor spaces with an explosion hazard of gases, vapors and flammable fogs mixed with air. Ex fluorescent light fitting type FLXE 118 is used as emergency fluorescent lighting fitting with one TC-TSE fluorescent compact lamp 18W with 2G11 lampholder. Housing: corrosion resistant grey polyurethanes painted aluminium color RAL 7000 Diffuser: borosilicate glass tube Gasket: Silicon caoutchouc The light fitting is normally supplied with two light sources, two entries M20 and wall/ sealing mounting set. Ex de IIC T5/T6 Ex d IIC T5/T6 tD A21 T90°C/T80°C, 230V , 60 Hz | piece | 2 | 0
5. | Series of wall luminaires for indoor and outdoor lighting, comprising:Body, trim, guard, screen and reflector made of self-extinguishing polycarbonate, ¬ frosted glass diffuser , aluminium reflector (incandescent version), stainless steel locking screws, 1x60 W, 231V, 60 Hz version is provided with low loss ballast polymer gasket, the magnetic ballasts installed in the fluorescent versions are equipped with thermal cut-off device, according to the EN 60598-1:2004 Standard, Tayp: NIKKO Visa Prisma | piece | 25 | 0
6. | Anti-panic lamp with polycarbonate diffuser, degree of protection IP42, with pictograms designed by, surface-mounted assembly 1x11W/min. 1h. | piece | 25 | 0
7. | Other unspecified material needed for the installation | kpl | 1 | 0
8. | Testing and functionality performed of the electrical installations | kpl | 1 | 0
TOTAL IV :
V) | INSTALATION FOR LIGHTNING
V.I) | GENERAL AND ANTI-PANIC LIGHTNING
5.1. | Making drains for general lighting power supply cable type PP-Y 3-5 x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 6 meters. | piece | 195 | 0
5.2. | Preparation of extracts for anti-panic lighting power supply cable type PP-Y 3x 1.5 mm2. The cables are laid on cable supports or clamp the false ceiling in the appropriate protective PVC hose. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. The average length of the feeder is 15 meters. | piece | 26 | 0
5.3. | Delivery and installation guides for lighting control type PP-Y 3x1, 5 mm2. Guides are placed partially in the cable carriers and partly in PVC tubing (60%). The price includes PVC pipes all together | met | 25 | 0
5.4. | Delivery and installation of hard SF 16 mm pipe to install lighting and other spaces without a suspended ceiling. Price includes clamps, connectors and junction boxes all together. | met | 25 | 0
5.5. | procurement and installation switches installation
| .simple water-proof p/ž | piece | 10 | 0
| .serial water-proof p/ž | piece | 18 | 0
| Control switch SMS 03/1 - switch actuator SMO 17/1 , - cable gland SPU 25, Type: SKX 12/21, TEP | piece | 2 | 0
| Ordinary mounting socket is 16A, 250 V, IP20 , 3P+E, enclosure shall begray, Type MIP-21 , TEP | piece | 2 | 0
| Ordinary duble mounting socket is 16A, 250 V, IP20 , 3P+E, enclosure shall begray, Type MIP-28 , TEP | piece | 15 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 73 | 0
| Mounting socket is 16A, 250 V, IP55 metal, 3P+E, enclosure shall begray, Type MMP-01 , TEP | piece | 1 | 0
| Mounting socket is 16A, 415 V, IP41 metal, 2P+E, enclosure shall begray, Type MMP-16 , TEP | piece | 1 | 0
11 | Other small material | flat | 1 | 0
12 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL V.1 :
VI) | INSTALLATIONS FOR OUTLETS AND POWER LINES
1 | Delivery and installation of conductors for outlet type and technology consumers PP-Y 3 x 2,5 mm2. Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 230 | 0
2 | Delivery and installation of conductors for outlet type PP-Y 5 x 2,5 mm2 . Conductors are placed on the cable carriers or clamps in false ceiling or in protective PVC pipes in plaster board. The price includes full installation materials and connecting cables, junction boxes and protective PVC pipe. | met | 730 | 0
4. | Delivery and installation solid pipe PN 16 mm outlets to install the service and other areas without a suspended ceiling. Price includes clamps, connectors and junction boxes. All together. | met | 50 | 0
5. | Delivery and installation of fixed single phase connection 16 A, mounting p/f | piece | 25 | 0
6. | Delivery and installation of fixed three-phase connection 16A, mounting p/f | piece | 5 | 0
7. | Connecting technological consumer (compressor,automatic regulation,...) with a cable to 4 mm2 | piece | 30 | 0
8. | Other small material | flat | 1 | 0
9. | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
TOTAL VI:
VII) | INSTALLATION OF POTENTIAL EQUALIZATION
1 | Delivery and installation and pulling in PVC pipes Φ 11 mm, P/F-Y 6 mm2 a conductor for making a compound of the pipeline water, heating and gas. The position includes the delivery and installation of connecting material such as clamps, bolts M 5x20 with nut, lugs, and more. The average length of the power line is 6 m. | piece | 1 | 0
2 | Delivery and installation and pulling in PVC pipes Φ 11. P/F 10 mm2 conductor for making a compound potential equalization to the closest distribution boards. The average length of the feeder is 15 m. | piece | 3 | 0
3 | Delivery and installation of boxes for the power line potential equalization | piece | 2 | 0
4 | Delivery and installation of conductor p/f 1x16 mm2 to connect an object with a mass of metal bus earth (PE), the nearest wiring closet. All together with lugs and clamps. | met | 4 | 0
5 | Delivery and installation copper cable 16 mm2 length 300 mm with cable lugs 16 mm2 at both ends of the bolts and nuts to bypass parts of the cable carrier. All together | piece | 7 | 0
6 | Creating bypass Gauge | piece | 2 | 0
7 | Delivery and installation of non-specified accessories | pšl | 1 | 0
8 | Testing of installed installations | pšl | 1 | 0
TOTAL VII:
VIII) | OUTDOOR LIGHTNING
Delivery and installation of cables for power supply lamp. Cables are laid partially in a ditch and partly to cable carriers in protective tube types are:
1 | Digging the earth in the soil category III for making the foundation pillars, 6m, complete with excess soil to landfill (0,8x0,8x1,0mx1 piece) | piece | 2 | 0
2 | Supply, delivery and dispersal of fine sand as a substrate for the cables in the trench (average 0,4x0,2) | m | 6 | 0
3. | Supply of concrete MB30 and the foundations for the pillars, 6m. Frame dimensions are based 80x80x100cm. A kit purchased from installing the appropriate anchor bolts and pipe Æ63 for introduction stub cables by the manufacturer of the stairs, the terms of the technical description and the drawings attached. | piece | 2 | 0
4. | Procurement of material and laying. PEHD pipe Ø63 mm
5. | SC 100, mast luminaire, primary light control with radial facetted optic, of aluminium, facetted, primary optical cover: cover panel, of toughened safety glass, transparent, light emission: direct distribution, installation type: post-top, side-entry, for 1 x HST 250W, superimposed pulse ignitor with auto. power-off, ballast: LLCG, with thermal protection switch, parallel p.f. corrected, with terminal, 3-pole, mains connection: 230V, AC, 60Hz, luminaire housing, upper part, of diecast aluminium, coated, grey aluminium (RAL 9007), length: 735 mm, width: 353 mm, height: 190mm, spigot size: 60/76mm (post-top) and 42/60mm (side-entry), luminaire housing, lower part, of diecast aluminium, coated, grey aluminium (RAL 9007), protection rating (complete): IP66, insulation class (complete): insulation class I (protective earthing), certification: CE, ENEC 10, VDE, standard: EN 50419, packaging unit: 1 piece, factory setting: LPV=4, RP=6 | piece | 2 | 0
6. | Supply and installation of the foundation on band crossings hot zinc coated tubular steel lighting pole segmental height h = 6m, with the opening of the terminal box complete with brackets for single-lamp at an angle of 100 (The appearance given in the draft attached to the project). Contractor's obligations to obtain statistical calculations and workshop drawings columns.
| -XP00-Y 4x4mm2 | m | 30 | 0
| -PP00-Y 3x2,5 mm2 | m. | 6 | 0
7 | Delivery and installation of the following material in the trench:
| -PVC Protectors of length 1 meter | piece | 30 | 0
| - PVC warning tape | met | 30 | 0
9 | Other small material for mounting and connecting | flat | 1 | 0
10 | Testing created installations with commissioning (putting into operation) | flat | 1 | 0
Note: Quote does not cover construction work on the excavation and backfilling the trench!
TOTAL VIII KM:
IX) | CONNECTION TO THE TELECOMMUNICATIONS INFRASTRUCTURE
1 | Deliver and lay the grout installation pipe with diameter 50 mm | m | 5 | 0
2 | Delivery and installation telephone terminal cabinets with metal doors with locks and built Crone blocks and cable head connecting cable TK | piece | 1 | 0
3 | Delivery and installation installer telephone cabinets with metal doors with locks and built Crone separating strip | piece | 1 | 0
4 | Perform a telephone connection box on the bus one potential GRO-including the necessary materials, complete | piece | 1 | 0
5. | Delivery and installation of communication outlet with two jacks RJ-45 CAT6. SOCKET | piece | 8 | 0
6. | Delivery and installation of UTP communication cable 4x2x0.5 mm Cat 6. Average lenght of cable is 25 meters. | piece | 8 | 0
7. | Delivery and installation of PVC flexible pipe for cable installation Ø16 mm including the necessary installation and connecting assembly equipment and materials (plaster, collars and ties). | piece | 8 | 0
| Acquisition, installation and connection of communication Gigabit Ethernet multilayer switch with the following characteristics: - 24x RJ-45 10/100BASE-T ports, IEEE 802.3/802.3u - 2x RJ-45 1000BASE-T ports, IEEE 802.3ab - 2x SFP GBIC ports - Folding capacity of 21.6 Gbits / s installation in 19" rack (1U) | piece | 1 | 0
TOTAL IX:
X) | SYSTEM FOR FIRE DETECTION
10.2. | MANUAL TRANSMITTER
1 | Hand conventional fire detector in red color to activate the fire extinguishing system, Ex proof EExde II CT6 tip BG2E MEDC Great Britain or similar one operating voltage do 250 V,- operating temperature from -20oC to the 50oC; IP 67 protection; manually activate the detector is provided with a single action (crush glass). Protective cover, metal, to prevent accidentally pressing buttons. Cable glands for Exd enclosure M25x15mm. Plugs for cable glands for Exd enclosure M25x15mm. | piece | 6 | 0
2. | Delivery and installation of addressable interactive multi-criterion automatic fire detectors (smoke-optical, thermal, thermo-differential), with algorithms and fuzzy logic, memory for false alarms, with a USB base 531-1, set, type MCD 573 SECURITON | piece | 2 | 0
3. | Delivery and installation of addressable modules with Ex barrier for galvanic separation, with two inputs, it is used to join the Ex-detector to the detector loop, type SCU81-3 SECURITON | piece | 1 | 0
4. | Delivery and installation of addressable automatic interactive multi-criterion Ex fire detectors, with algorithms and fuzzy logic, memory for false alarms, type and ORM130 Ex-SECURITON | piece | 2 | 0
5. | Delivery and installation of addressable branch module, it is used to join the smoke sampling and analysing system and stable extinguishing system control unit to the detector loop, type SCI81 SECURITON | piece | 19 | 0
6. | Delivery and installation of addressible input / output module 5OUT/3IN for decentralized management of various functions (fire doors, ventilators, air-conditioning systems, lifts, etc..) It is used for monitoring with 5 control contacts NO / NC 50VDC-1A and monitoring of 0 voltage devices with contacts NO or NC (sprinkler, classic fire detectors etc..), connection to the device is controlled, it is mounted on a wall or ceiling, i has a protection IP40, 24VDC power from the loop, ROM81A SECURITON | piece | 2 | 0
7. | Delivery and installation of a chamber for analysis of smoke samples in the air-ventilation channels, passive without their own fans, with mechanical indicator for air flow, with sample perforated pipe length of 1500 mm for channel width of 800-1400 mm with analog addressable optical-smoke detectors with increased sensitivity, type LKM531 SECURITON | piece | 2 | 0
8. | Delivery and installation of special detectors for the analysis of air in 19''rack cabinets, type ASD516-1 SECURITON | piece | 1 | 0
9. | Delivery and installation of not combustible red cable JBY (St) Y2x2x0, 8mm for connection of addressable fire detection elements on the loop. Average length of cable between elements is 12 m. | piece | 20 | 0
10. | Supply and delivery of mark elements for the fire alarm system | piece | 12 | 0
11. | Complete programming and configuration of fire alarm system main control unit, making interaction algorithms with other systems and test of all functions of the system according to the project and specific requirements | complet | 1 | 0
12. | Commissioning and testing system to the level of full functionality, including interactions with integrated systems of ISM (access control, video surveillance, etc.) | complet | 1 | 0
13. | Training employees to handle fire alarm system including the manufacturers instructions | complet | 1 | 0
14. | Testing the functionality of the fire alarm system by authorized company and the issuance of Certificate | complet | 1 | 0
15. | Addressable input module with eight inputs, for connecting the flame detector to the central system, addressable fire alarm signal system starts to work on the fire, the type of MDI 82 Securiton Switzerland. The module has VdS attest. | piece | 1 | 0
16. | Metal carrier for mounting one handheld detector to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 4 | 0
17. | Marking elements with persistent marks | piece | 7 | 0
18. | Other unspecified fine material. | kpl. | 1 | 0
19. | Installation and connection of the detector, all the EX version. | kpl. | 4 | 0
TOTAL MANUAL TRANSMITTER
9.3. | SIREN
1. | Siren type Medco DB3P or similar, Exd enclosure, strength, anti-Static material, 115 DB, IP 66/67, ATEX Exde, operating voltage od 12Vd.c.-240Va.c, 27 adjustable tone Producer MEDC Great Britain
2 | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 5 | 0
3. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists. Delivery and installation. | piece | 5 | 0
4. | Cable glands for Exd enclosure M25x15mm. | piece | 5 | 0
5. | Plugs for cable glands za Exd enclosure M25x15mm. | piece | 5 | 0
6. | Marking elements with persistant marks | piece | 5 | 0
7. | Installation and connection of sirens, all the Ex version. | kpl. | 5 | 0
TOTAL SIRENS :
9.4. | FLASHES
1. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Red. | piece | 3 | 0
2. | Flash in red, type Medco XB9 or similar, Xenon flash light intensity 5 Joule, a GRP impact resistant conductive material, ATEX certified Ex II 2G, Zone 1 EExd IIC T6, IP66 & 67, Voltage: 24Vd.c.-240Va.c., flashing frequency: 60/min, lens color: Blue | pieces | 3 | 0
3. | Addressable command module to activate the fire alarm system via COM 81 Securiton Switzerland or similar. | piece | 3 | 0
4. | Metal carrier for mounting one handheld detectors to construct the facility, with a stand, with painted canopy, placed by welding or screw to the joists.Delivery and installation. | piece | 3 | 0
5. | Marking elements with persistant marks | piece | 3 | 0
6. | Installation and connection of flash, all the EX version. | kpl. | 3 | 0
TOTAL FLASHES:
9.5. | CONTROL UNIT FOR FIRE ALARM
Equipment must be fully integrated and compatible with the existing decentralized system SecuriPro fire alarm equipment supplied must match types in the specification or be equivalentna.
1. | Microprocessor addressable fire panels for signaling, type MCU 211 Securiton Switzerland or similar, for building interactive SecuriPro fire alarm systems, addressable capacity of 4 loops with 127 addressable interactive SecuriStar detector in each loop | kpl. | 1 | 0
Operator should have integrated LAN interface (SecuriLan) based on Echelon LONWORKS technology, which allows you to connect with other exchanges and parallel MCU operating consoles, serial interface modules, relay output modules, the parallel interface modules and similar.
The Central via SecuriLine loop linking addressable automatic and manual call points and input-output modules. Switchboard MCU 211 provides power supply and continuous monitoring signal - javljačkih lines, signaling tripping signal lines or the occurrence of the fault on them, sending alarm signals to the acoustic source, such as management and specific interventions by the two-level alarm level.
Ther Central provides the signals necessary to connect the system with other fire signaling systems (executive function control panel). Exchange has programmable relay outputs for switching alarms, excluding ventilation, electricity, doors PP, PP flap or the like in the case of fire.
Operator has the ability to command a stable systems for automatic fire extinguisher.
Central has the ability to perform a software selection criterion of sensitivity and fire detectors (smoke, temperature / speed of temperature rise or a mixture).
Mounted in a separate enclosure with power supply unit for power supply and a rechargeable battery 2x12V, 26Ah for backup power supply system at least 72 hours in quiet and 30 minutes in alarm mode. Produced by "Securiton", Switzerland. The modules have VdS approval.
2. | Expansion Module central unit with open-collector output Spiece OCB 71 Securiton Switzerland or equivalent, with 32 open collector outputs.
| EasyLon Amplifier module for allowing of extension of the communication line between the exchanges of fire, up to 2700m, type 811 SLR "Securiton" Switzerland or similar. It is mounted in the enclosure of the existing plant in the firehouse or existing distribution cabinet. | piece | 1 | 0
| Delivery, installation and connection of distribution cabinet (for the power supply) alarm siren and strobe light. Cabinet is for wall mounting, two times pickled sheet metal, dimensions (WxHxD) 1000x800x250mm, with door and key, with a metal mounting plate, with 10 and 8 M25x1.5mm glands glands M63x1.5mm. | piece | 1 | 0
| Cabinet includes: | piece | 1 | 0
·1 piece of the torus transformer 220Vac /24Vdc,
·1 piece of the Power supply unit 24V, 5A,
·1 piece of the rechargeable battery 2x12V, 7,2Ah,
·1 piece of the automatic fuse 6A,
·relay vard with three relays 24V/2A
·40 pieces of Two-stairs VS terminals 1.5mm2,
·spaces for safety barriers
·spaces for MDI module
·spaces for SOM module
·1 piece of the. DIN šina,
·perforated tiles with lid
·other unspecified fine material
Complete with accessories to connect the equipment and the wall.
3. | Addressable input module with a single input, the transmission of information to SecuriPro loop addressable fire alarm system, the type of SDI 82 Securiton Switzerland. The module has VdS approval. | piece | 2 | 0
4. | Marking elements with persistent marks | piece | 2 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of the flame detector, all the EX version. | kpl. | 1 | 0
7. | ATTESTS FOR EX EQUIPMENT
Creating attests authorized by the domestic industry.
9.6. | INSTALLATION EQUIPMENT AND MATERIAL
1. | Delivery and installation distribution cabinet, high quality steel material STAINLESS STEEL type Stahl 1,4301, AISI 304, IP 66, Ex-protection: Ex de II T 6, for Ex zone 1 I 2, equipped with:
| outing plate glands from the upper and lower sides, | piece | 1 | 0
cable glands or plugs M25x1.5 Ex design, minimum 25 pieces
cable glands or plugs M63x1.5mm Ex design, minimum 4 pieces
and order clamps minimum 50 pieces
Mounts on existing carriers in drive:
2. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 300x50mm. | m | 30 | 0
3. | Delivery and installation of metal cabinets, complete with accessories for mounting (brackets, curves ...), dimensions: 50x50mm. | m | 4 | 0
4. | 2'' metal pipe, galvanized, welded pipe for laying the cable. There is a welding or suitable means for steel construction. | m | 10 | 0
5. | Other unspecified fine material. | kpl. | 1 | 0
6. | Installation and connection of equipment | kpl. | 1 | 0
9.7. | CABLE INSTALLATION
1. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the manual detectors, from the control room of the command to the appropriate JB junction box
2. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the gas detectors, from the control room of the command to the appropriate JB junction box | m. | 10 | 0
3. | Delivery and installation cable LiHCH 3x1,5 mm2 flame retardant or similar - to connect the flame detectors, from the control room of the command to the appropriate JB junction box | m. | 10 | 0
4. | Delivery and installation cable VO-YMvKmbas 24x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 10 | 0
5. | Delivery and installation cable VO-YMvKmbas 16x1,5 mm2 flame retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 10 | 0
6. | Delivery and installation cable LiHCH 3x1,5 mm2 flame mm2 retardant or similar - to connect the sirens and flashes, from the control room of the command to the appropriate JB junction box | m. | 7 | 0
7. | Delivery and installation of cable NXHXH 3x2,5 or similar - to connect to the central fire detection unit and an additional power supply unit with a control panel for the main power supply to the building electrical room. | m. | 10 | 0
8. | Delivery and installation cable PF 4mm2 or similar grounding unit enclosure to the nearest grounded point in the drive. | m. | 15 | 0
9. | Other unspecified fine material. | m. | 15 | 0
9.8. | COMMISSIONING (START UP)
1. | . checking the correctness of system installed and assembled elements, | kpl. | 1 | 0
.installation and connection switchboard ( the Central) to the network,
.marking equipment
.mounting the detector signal lines on the switchboard,
Programming switchboard, testing and commissioning,
.user training for the handling,
. delivery of documentation (manual handling and programming, diary devices and certificates)
. Handover and assembling the record on safety and functional testing.
TOTAL COMMISSIONING :
TOTAL IX
X) | LIGHTNING ROD INSTALLATION
Lightening rod installations of the building prevents a direct lightning strike to the building and possible damage caused by a fire due to electrostatic discharge.
Roof racks for metal covers (every 80 cm along the wall and cover the sandwich panels):
| SON 16-K | pieces | 163 | 0
Roof equipment:
Wall cabinet for measurement:
| ZON 05, Rf 20522 | pieces | 9 | 0
Wall brackets (for the height difference):
| ZON 03, Rf20322 | pieces | 2 | 0
Contact elements:
Bonding wire-wire connectors:
| KON 08; Rf 50111 | pieces | 9 | 0
Tags for measuring site:
| MŠ , Rf 80 122 | pieces | 9 | 0
Measuring tape-wire connectors:
| KON 02, Rf 40 122 | pieces | 6 | 0
Drip:
| KON 21; Rf 200212 | pieces | 6 | 0
Impact point-Spitz:
| LOV Rf 300400 | pieces | 4 | 0
Interlocking Coupler (for horizontal gutters):
| KON 06 Rf 60122 | pieces | 10 | 0
Contact connectors (for grounding metal mass inside the building)
| KON 05; Rf 80529 | pieces | 6 | 0
Contact connectors (for switching cathing sticks to the strip grounding):
| KON 07; Rf 40611 | pieces | 4 | 0
Lightning conductor:
Conductor prochrome RH 3 FI 8 mm (downhill and through the roof of a divorce):
| RH 3 ; Rf 90150 | m | 180 | 0
Grounding:
Strip grounding 30 x 3.5 mm (basic grounding + rampart):
| RH 1; Rf 90701 | m | 240 | 0
Crossing coupling tape-tape:
| KON 01; Rf 50422 | kpl | 30 | 0
Crossing coupling strip-Reinforcing steel (every 2 m):
| KON 09; Rf 90122 | kpl | 110 | 0
RECOMMENDED:
IEC 62305
Overvoltage Protection prevents damages caused BY overvoltage currents which come into the building through a "doorway" installation (power supply, antenna, cable and telephone operators, etc.) and, caused by direct or (most common form) indirect lightning.
TOTAL X :
XI) | TEST AND MEASURMENT
1 | Measurement and Testing & functionality created electrical installations with the release of the testing report (performed by the authorized person)
| TOTAL XI : | kpl | 1 | 0
XII) | PROJECT OF CREATED STATE
1 | Project of created state for electrical installations for high current is created in two copies and electronically and submitted investor.
| TOTAL XII : | kpl | 1 | 0
ELECTRICAL INSTALLATIONS - Recapitulation
I) | DISTRIBUTION CABINETS
II) | POWER CABLES
III) | CABLE CARRIERS AND INSTALLATION PIPES
IV) | FLASHLIGHTS
V) | ILIGHTNING INSTALLATION
VI) | OUTLET AND FEEDER INSTALLATIONS
VII) | POTENTIAL EQUALIZING INSTALLATIONS
VIII) | CONNECTION TO TELEPHONE INFRASTRUCTURE
IX) | FIRE DETECTION SYSTEM
X) | LIGHTNING ROD INSTALLATION
XI) | TESTING AND MESAURING
XII) | PROJECT OF CREATED STATE
TOTAL